TM

OLE for Process Control

Data Access Standard

(UPDATED)

Version

September 11, 1997

Synopsis:

| This specification is the specification of the interface for developers of OPC clients and OPC servers.. The specification is a result of an analysis and design process to develop a standard interface to facilitate the development of servers and clients by multiple vendors that shall inter-operate seamlessly together. Specificationation Type | Industry Standard Specification |  |  |  |
| --- | --- | --- | --- | --- |
| Title: | OLE for Process Control ( OPC ) | Date: |  |  |
| Version: |  | Soft | MS-Word |  |
|  |  | Source: | input.doc |  |
| Author: | Opc Foundation | Status: | Final |  |

Trademarks:

Most computer and software brand names have trademarks or registered trademarks. The individual trademarks have not been listed here.

Required Runtime Environment:

This specification requires Windows 95, Windows NT 4.0 or later

NON-EXCLUSIVE LICENSE AGREEMENT

The OPC Foundation, a non-profit corporation (the “OPC Foundation”), has established a set of standard OLE/COM interface protocols intended to foster greater interoperability between automation/control applications, field systems/devices, and business/office applications in the process control industry.

The current OPC specifications, prototype software examples and related documentation (collectively, the “OPC Materials”), form a set of standard OLE/COM interface protocols based upon the functional requirements of Microsoft’s OLE/COM technology.  Such technology defines standard objects, methods, and properties for servers of real-time information like distributed process systems, programmable logic controllers, smart field devices and analyzers in order to communicate the information that such servers contain to standard OLE/COM compliant technologies enabled devices (e.g., servers, applications, etc.).

The OPC Foundation will grant to you (the “User”), whether an individual or legal entity, a license to use, and provide User with a copy of, the current version of the OPC Materials so long as User abides by the terms contained in this Non-Exclusive License Agreement (“Agreement”).  If User does not agree to the terms and conditions contained in this Agreement, the OPC Materials may not be used, and all copies (in all formats) of such materials in User’s possession must either be destroyed or returned to the OPC Foundation. By using the OPC Materials, User (including any employees and agents of User) agrees to be bound by the terms of this Agreement.

LICENSE GRANT:

Subject to the terms and conditions of this Agreement, the OPC Foundation hereby grants to User a non-exclusive, royalty-free, limited license to use, copy, display and distribute the OPC Materials in order to make, use, sell or otherwise distribute any products and/or product literature that are compliant with the standards included in the OPC Materials.

All copies of the OPC Materials made and/or distributed by User must include all copyright and other proprietary rights notices include on or in the copy of such materials provided to User by the OPC Foundation.

The OPC Foundation shall retain all right, title and interest (including, without limitation, the copyrights) in the OPC Materials, subject to the limited license granted to User under this Agreement.

WARRANTY AND LIABILITY DISCLAIMERS:

User acknowledges that the OPC Foundation has provided the OPC Materials for informational purposes only in order to help User understand Microsoft’s OLE/COM technology.  THE OPC MATERIALS ARE PROVIDED “AS IS” WITHOUT WARRANTY OF ANY KIND, EXPRESS OR IMPLIED, INCLUDING, BUT NOT LIMITED TO, WARRANTIES OF PERFORMANCE, MERCHANTABILITY, FITNESS FOR A PARTICULAR PURPOSE OR NON-INFRINGEMENT.  USER BEARS ALL RISK RELATING TO QUALITY, DESIGN, USE AND PERFORMANCE OF THE OPC MATERIALS.  The OPC Foundation and its members do not warrant that the OPC Materials, their design or their use will meet User’s requirements, operate without interruption or be error free.

IN NO EVENT SHALL THE OPC FOUNDATION, ITS MEMBERS, OR ANY THIRD PARTY BE LIABLE FOR ANY COSTS, EXPENSES, LOSSES, DAMAGES (INCLUDING, BUT NOT LIMITED TO, DIRECT, INDIRECT, CONSEQUENTIAL, INCIDENTAL, SPECIAL OR PUNITIVE DAMAGES) OR INJURIES INCURRED BY USER OR ANY THIRD PARTY AS A RESULT OF THIS AGREEMENT OR ANY USE OF THE OPC MATERIALS.

GENERAL PROVISIONS:

This Agreement and User’s license to the OPC Materials shall be terminated (a) by User ceasing all use of the OPC Materials, (b) by User obtaining a superseding version of the OPC Materials, or (c) by the OPC Foundation, at its option, if User commits a material breach hereof.  Upon any termination of this Agreement, User shall immediately cease all use of the OPC Materials, destroy all copies thereof then in its possession and take such other actions as the OPC Foundation may reasonably request to ensure that no copies of the OPC Materials licensed under this Agreement remain in its possession.

User shall not export or re-export the OPC Materials or any product produced directly by the use thereof to any person or destination that is not authorized to receive them under the export control laws and regulations of the United States.

The Software and Documentation are provided with Restricted Rights.  Use, duplication or disclosure by the U.S. government is subject to restrictions as set forth in (a) this Agreement pursuant to DFARs 227.7202-3(a); (b) subparagraph (c)(1)(i) of the Rights in Technical Data and Computer Software clause at DFARs 252.227-7013; or (c) the Commercial Computer Software Restricted Rights clause at FAR 52.227-19 subdivision (c)(1) and (2), as applicable.  Contractor/ manufacturer is the OPC Foundation, P.O. Box 140524, Austin, Texas 78714-0524.

Should any provision of this Agreement be held to be void, invalid, unenforceable or illegal by a court, the validity and enforceability of the other provisions shall not be affected thereby.

This Agreement shall be governed by and construed under the laws of the State of Minnesota, excluding its choice or law rules.

This Agreement embodies the entire understanding between the parties with respect to, and supersedes any prior understanding or agreement (oral or written) relating to, the OPC Materials.

Revision 1.0A Highlights

This revision includes numerous clarifications and a few corrections to the 1.0 Specification. Although changes were made throughout the document, the following areas are or particular importance:

- Clarification of Read and Write operations as related to Active status of Group and Items.

- Clarification of Async operations under various error conditions.

- Clarification of AddItems error handling for BADTYPE.

- Removal of IEnumUnknown from the OPCServer.

- Modification of CreateGroupEnumerator.

- Correction of BSTR marshalling issues.

- Correction of ACCESSRIGHTS in IDL.

Table of Contents

1. Introduction

1.1 Background

1.2 Purpose

1.2.1 The Current Client Application Architecture

1.2.2 The Custom Application Architecture

1.2.3 General

1.3 Scope

1.4 References

1.5 Audience

1.6 Deliverables

2. OPC Fundamentals

2.1 OPC Overview

2.2 Where OPC Fits

2.3 General OPC Architecture and Components

2.4 Overview of the Objects and Interfaces

2.5 Required Interface Definition

2.6 Optional Interface Definition

2.7 Which interface should the client application use.

2.8 The Address Space and Configuration of the Server

2.9 Local vs. Remote Servers

2.10 Application Level Server and Network Node Selection

2.11 UNICODE, NT and WIN95

2.12 Threads and Multitasking

2.13 Synchronization and Serialization Issues

2.14 Public (aka shared) Groups

2.15 Persistent  Storage Story

3. OPC Quick Reference

3.1 Custom Interface

3.1.1 OPCServer Object

3.1.2 OPCGroup Object

3.1.3 EnumOPCItemAttributes Object

3.2 Custom Interface/Client Side

3.3 Automation Interface

3.3.1 OPCServer Object

3.3.2 OPCGroup Object

3.3.3 OPCItem Object

3.4 Automation Interface/Client Side

4. OPC Custom Interface

4.1 Overview of the OPC Custom Interface

4.2 General Information

4.2.1 Ownership of memory

4.2.2 Standard Interfaces

4.2.3 Null Strings and Null Pointers

4.2.4 Returned Arrays

4.2.5 Public Groups

4.2.6 CACHE data and DEVICE data

4.2.7 Asynchronous vs. Synchronous Interfaces

4.2.8 The ACTIVE flags, Deadband and Update Rate

4.2.9 Data Acquisition and Active State Behavior

4.2.10 Errors and return codes

4.3 OPCServer Object

4.3.1 Overview

4.3.2 IUnknown

4.3.3 IOPCServer

4.3.4 IOPCServerPublicGroups (optional)

4.3.5 IOPCBrowseServerAddressSpace (optional)

4.3.6 IPersistFile (optional)

4.4 OPCGroup Object

4.4.1 General Properties

4.4.2 IOPCItemMgt

4.4.3 IOPCGroupStateMgt

4.4.4 IOPCPublicGroupStateMgt

4.4.5 IOPCSyncIO

4.4.6 IOPCAsyncIO

4.4.7 IEnumOPCItemAttributes

4.4.8 IDataObject

4.5 Client Side Interfaces

4.5.1 IAdviseSink

5. OPC Automation Interface Design

5.1 Overview

5.2 OPC Server Object

5.2.1 IOPCServerDisp Interface

5.2.2 IOPCServerPublicGroupsDisp

5.2.3 IOPCServerBrowseServerAddressSpaceDisp Interface

5.3 OPCGroup

5.3.1 IOPCItemMgtDisp Interface

5.3.2 OPCGroup as IOPCGroupStateMgtDisp

5.3.3 OPCGroup as IOPCSyncIODisp

5.3.4 OPCGroup as IOPCASyncIODisp

5.3.5 OPCGroup as IOPCPublicGroupStateMgtDisp

5.4 OPCItem Object

5.4.1 OPCItem as IOPCItemDisp

5.5 Exception and Asynchronous Notifications - Client Side

6. Installation Issues

6.1 Registry Entries for Custom Interface

6.2 Registry Entries for the Proxy/Stub DLL

6.3 Registry Entries for Automation Interface

6.4 Creating the Registry Entries

6.5 Registry Entries and DCOM

7. Description of Data Types, Parameters and Structures

7.1 Item Definition

7.2 AccessPath

7.3 Blob

7.4 Time Stamps

7.5 Variant Data Types for OPC Data Items

7.6 Constants

7.6.1 OPCHANDLE

7.7 Structures and Masks

7.7.1 OPCITEMSTATE

7.7.2 OPCITEMDEF

7.7.3 OPCITEMRESULT

7.7.4 OPCITEMATTRIBUTES

7.7.5 OPCSERVERSTATUS

7.7.6 Access Rights

7.8 OPC Quality flags

7.9 Data Stream Formats

7.9.1 OPCGROUPHEADER

7.9.2 OPCITEMHEADER1

7.9.3 OPCITEMHEADER2

7.9.4 OPCGROUPHEADERWRITE

7.9.5 OPCITEMHEADERWRITE

7.9.6 Marshaling the Data (Variants) into the Stream

8. Summary of OPC Error Codes

9. OPCError.h

10. Appendix A - IDL Specification

11. Appendix B - ODL Specification

# Introduction

## Background

A standard mechanism for communicating to numerous data sources, either devices on the factory floor, or a database in a control room is the motivation for this specification.

The information architecture for the Process Industry shown in Figure 1-1 involves the following levels:

Field Management. With the advent of “smart” field devices, a wealth of information can be provided concerning field devices that has was not previously available. This information provides data on the health of a device, its configuration parameters, materials of construction, etc. All this information must be presented to the user, and any applications using it, in a consistent manner.

Process Management. The installation of Distributed Control Systems (DCS) and SCADA systems to monitor and control manufacturing processes makes data available electronically which had been gathered manually.

Business Management. Benefits can be gained by installing the control systems. This is accomplished by integrating the information collected from the process into the business systems managing the financial aspects of the manufacturing process. Providing this information in a consistent manner to client applications minimizes the effort required to provide this integration.

To do these things effectively, manufacturers need to access data from the plant floor and integrate it into their existing business systems. Manufacturers must be able to utilize off the shelf tools (SCADA Packages, Databases, spreadsheets, etc.) to assemble a system to meet their needs. The key is an open and effective communication architecture concentrating on data access, and not the types of data.

Purpose

Figure 1-1 Process Control Information Architecture

What is needed is a common way for applications to access data from any data source like a device or a database.

Figure 1-2.  Applications Working with Many OPC Servers

### The Current Client Application Architecture

There are many client applications that have been developed that require data from a data source and access that data by independently developing “Drivers” for their own packages.

This leads to the problems that follow:

- Much duplication of effort

- Everyone must write a driver for a particular vendor’s hardware.

- Inconsistencies between vendors drivers

- Hardware features not supported by all driver developers.

- Support for hardware feature changes

- A change in the hardware’s capabilities may break some drivers

- Access Conflicts

- Two packages generally cannot access the same device simultaneously since they each contain independent Drivers.

Hardware manufacturers attempt to resolve these problems by developing drivers, but are hindered by differences in client protocols. Today they cannot develop an efficient driver that can be used by all clients.

OLE for Process Control (OPCä) draws a line between hardware providers and software developers. It provides a mechanism to provide data from a data source and communicate the data to any client application in a standard way.  A vendor can now develop a reusable, highly optimized server to communicate to the data source, and maintain the mechanism to access data from the data source/device efficiently. Providing the server with an OPC interface allows any client to access their devices.

### The Custom Application Architecture

A growing number of custom applications  are being developed in environments like Visual Basic (VB), Delphi, Power Builder, etc. OPC must take this trend into account. Microsoft understands this trend and designed OLE/COM to allow components (written in C and C++ by experts in a specific domain) to be utilized by a custom program (written in VB or Delphi for an entirely different domain). Developers will write software components in C and C++ to encapsulate the intricacies of accessing data from a device, so that business application developers can write code in VB that requests and utilizes plant floor data.

The intent of this specification is to facilitate the development of OPC Servers in C and C++, and to facilitate development of OPC client applications in the language of choice.

The architecture and design of the interfaces described in this specification are intended to support development of OPC servers in other languages as well.

### General

OLE for Process Control (OPC™) is designed to allow client applications access to plant floor data in a consistent manner. With wide industry acceptance OPC will provide many benefits:

- Hardware manufacturers only have to make one set of software components for customers to utilize in their applications.

- Software developers will not have to rewrite drivers because of feature changes or additions in a new hardware release.

- Customers will have more choices with which to develop World Class integrated manufacturing systems.

With OPC, system integration in a heterogeneous computing environment will become simple. Leveraging OLE/COM the environment shown in Figure 1-3 becomes possible.

Figure 1-3. Heterogeneous Computing Environment

## Scope

A primary goal for this document was to deliver a specification to the industry as quickly as possible. With this in mind, the scope of the this document is limited to areas common to all vendors. The intent is to define additional functionality in future releases. Therefore, this release focuses on the efficient reading and writing of data between an application and a process control device flexibly and efficiently. Functionality such as alarm handling, security, and historical data access are also intended to be addressed in subsequent releases.  The architecture of OPC leverages the advantages of the COM interface, which provides a convenient mechanism to extend the functionality of OPC.

Other goals for the design of OPC were as follows:

- simple to implement

- flexible to accommodate multiple vendor needs

- provide a high level of functionality

- allow for efficient operation

This specification includes the following:

- A set of custom COM interfaces for use by client and server writers.

- A set of OLE Automation interfaces to support clients developed with higher level business applications such as Excel, Visual Basic, etc. We expect that with the current revision of the OPC specification clients and servers will be written in C++, although Visual Basic applications can interface to the custom interface via a variety of mechanisms.

- The current specification does not explicitly address clients and servers operating on different nodes. The architecture and specification of the interfaces was designed to accommodate the distributed architecture. In addition, the architecture is intended to utilize the Microsoft distributed OLE technology (DCOM) to facilitate clients interfacing to remote servers.

## References

Kraig Brockschmidt ,Inside OLE, Second Edition, Microsoft Press, Redmond, WA, 1995.

Microsoft COM Specification, version 0.9, 10/24/95  (available from Microsoft’s FTP site).

Microsoft Systems Journal, Q&A, April, 1996, pp. 89-101.

OLE Automation Programming Reference, Microsoft Press, Redmond, WA, 1996.

OLE 2 Programming Reference, Vol. 1, Microsoft Press, Redmond, WA, 1994.

In general we should only list those references that are required reading to be able to effectively use the specification.

## Audience

This specification is intended to be used as reference material for developers of OPC compliant Clients and Servers. It is assumed that the reader is familiar with Microsoft OLE/COM technology and the needs of the Process Control industry.

This specification is inteded to facilitate development of OPC Servers in C and C++, and of  OPC client applications in the language of choice.  Therefore, the developer of the respective component is expected to be fluent in the technology required for the specific component.

## Deliverables

The deliverables from the OPC Foundation with respect to the OPC Specification include the OPC Specification itself, OPC IDL and ODL files (included in this document as Appendicies) and the OPC Error header files (included in this document). Note that the ‘generic’ OPC Header file (OPC.H) can be generated directly from the IDL file contained in this document.

This specification covers the analysis and design of COM compliant custom interfaces and an OLE Automation interface.

This specification contains design information for the following:

- The OPC COM custom interface -  This document will describe the Interfaces and Methods of OPC Components and Objects.

- The OPC OLE Automation interface -  This document will also describe the OPC Automation Interfaces which facilitate the use of Visual Basic, Delphi and other Automation enabled products to interface with OPC Servers.

# OPC Fundamentals

OPC is based on Microsoft’s OLE/COM technology.

## OPC Overview

This specification describes the OPC COM Objects and their interfaces implemented by OPC Servers.  An OPC Client can connect to OPC Servers provided by one or more vendors.

Figure 2-1 OPC Client

OPC Servers may be provided by different vendors. Vendor supplied code determines the devices and data to which each server has access, the data names, and the details about how the server physically accesses that data. Specifics on naming conventions are supplied in a subsequent section.

Figure 2-2 OPC Client/Server Relationship

At a high level, an OPC server is comprised of several objects: the server, the group, and the item.  The OPC server object maintains information about the server and serves as a container for OPC group objects.  The OPC group object maintains information about itself and provides the mechanism for containing and logically organizing OPC items.

The OPC Groups provide a way for clients to organize data.  For example, the group might represent items in a particular operator display or report.  Data can be read and written.  Exception based connections can also be created between the client and the items in the group and can be enabled and disabled as needed.  An OPC client can configure the rate that an OPC server should provide the data changes to the OPC cleint.

There are two types of groups, public and local (or ‘private’). Public is for sharing across multiple clients, local is local to a client.  Refer to the section on public groups for the intent, purpose, and functionality and for further details.  There are also specific optional interfaces for the public groups.

Within each Group the client can define one or more OPC Items.

Figure 2-3 - Group/Item Relationship

The OPC Items represent connections to data sources within the server. An OPC Item, from the custom interface perspective, is not accessible as an object by an OPC Client. Therefore, there is no external interface defined for an OPC Item.  All access to OPC Items is via an OPC Group object that “contains” the OPC item, or simply where the OPC Item is defined.

Associated with each item is a Value, Quality and Time Stamp.  The value is in the form of a VARIANT, and the Quality is similar to that specified by Fieldbus.

Note that the items are not the data sources - they are just connections to them.  For example, the tags in a DCS system exist regardless of whether an OPC client is currently accessing them.  The OPC Item should be thought of as simply specifying the address of the data, not as the actual physical source of the data that the address references.

## Where OPC Fits

Although OPC is primarily designed for accessing data from a networked server, OPC interfaces can be used in many places within an application. At the lowest level they can get raw data from the physical devices into a SCADA or DCS, or from the SCADA or DCS system into the application.. The architecture and design makes it possible to construct an OPC Server which allows a client application to access data from many  OPC Servers provided by many different OPC vendors running on different nodes via a single object.

Figure 2-4 - OPC Client/Server Relationship

## General OPC Architecture and Components

OPC is a specification for two sets of interfaces; the OPC Custom Interfaces and the OPC Automation interfaces.  A revised automation interface will be provided with release 2.0 of the OPC specification. This is shown in Figure 2-5.

Figure 2-5 - The OPC Interfaces

The OPC Specification specifies COM interfaces (what the interfaces are), not the implementation (not the how of the implementation) of those interfaces. It specifies the behavior that the interfaces are expected to provide to the client applications that use them.

Included are descriptions of architectures and interfaces that seemed most appropriate for those architectures. Like all COM implementations, the architecture of OPC is a client-server model where the OPC Server component provides an interface to the OPC objects and manages them.

There are several unique considerations in implementing an OPC Server. The main issue is the frequency of data transfer over non-sharable communications paths to physical devices. Thus, we expect that the OPC Server will either be a local or remote EXE which includes code that is responsible for efficient data collection from a physical device.

An OPC client application communicates to an OPC server through the specified OPC custom and automation interfaces.  OPC servers must implement the custom interface, and optionally may implement the automation interface.

An inproc (OPC handler)  may be used to marshal the interface and provide the additional Item level functionality of the OPC Automation Interface.  Refer to the figure Typical OPC Architecture.

Figure 2-6 - Typical OPC Architecture

It is also expected  that the server  will consolidate and optimize data accesses requested by the various clients to promote efficient communications with the physical device.  For inputs (Reads), data returned by the device will be buffered for asynchronous distribution or synchronous collection by various OPC clients.  For outputs (writes), the OPC Server updates the physical device data on behalf of OPC Clients.

## Overview of the Objects and Interfaces

The OPC Server object provides a way to access (read/write) or communicate to a set of data sources.. The types of sources available are a function of the server implementation.

An OPC client connects to an OPC server and communicates to the OPC server through the interfaces.  The OPC server object provides functionality to an OPC client to create and manipulate OPC group objects. These groups allow clients to organize the data they want to access. A group can be activated and deactivated as a unit. A group also provides a way for the client to ‘subscribe’ to the list of items so that it can be notified when they change.

Note: All COM objects are accessed through Interfaces. The client sees only the interfaces. Thus, the objects described here are ‘logical’ representations which may not have anything to do with the actual internal implementation of the server. The following figure is a summary of the OPC Objects and their interfaces.  Note that some of the interfaces are Optional (as indicated by [  ]).

Figure 2-7 - Standard OPC Server Object

Figure 2-8 - Standard OPC Group Object

Figure 2-9 - Standard (Automation) OPC Item Object (to be defined in a subsequent release)

## Required Interface Definition

OPC server developers must implement all functionality of required interfaces. An OPC client ommunicates to an OPC server by calling functions from the OPC required interfaces.

## Optional Interface Definition

OPC server developers may implement the functionality of the optional interfaces

An optional interface is one that the server developer may elect to implement. When an OPC Server supports an optional interface, all functions within that optional interface must be implemented, even if the function just returns E_NOTIMPL. An OPC client that wishes to use the functionality of an optional interface will query the OPC server for the optional interface.  The client must be designed to not require that this optional interface exist.

## Which interface should the client application use.

In general, client programs which are created using scripting languages will use the automation interface.  Client programs which are created in C++  will find it easiest to use the custom interface for maximum performance.

## The Address Space and Configuration of the Server

This release of the OPC specification assumes that a server configuration address space may be managed and persistently stored using the IPersistFile interface.  Only the server specific information is persistently stored.  All client configuration information (Group and Item Definitions) must be persistently stored by the respective client application.  All Handles that are defined in the system are not guaranteed to have the same value between sessions of the client and server conversation.

It is important to distinguish the address space of the server (also known as the server configuration) from the small subsets of this space that a particular client may be interested in at a particular time (also known as the ‘groups’ and ‘items’).  The details of how these client specific groups are maintained is discussed in detail in this specification.  The persistent storage of groups is the responsibility of the respective clients.  The details of how the server address space is defined and configured are intentionally left unspecified.  For example the server address space might be:

- Entirely fixed (e.g. for a dedicated interface to a particular device such as a scale).

- Configured entirely outside of the OPC environment (e.g. for an interface to an existing external DCS system).

- Automatically configured at startup by an ‘intelligent’ server which can poll the existing system for installed hardware or interfaces.

- Automatically configured on the fly by an ‘intelligent’ server based on the names of the data items the client applications are currently requesting.

It is expected that this server address space is stable and is managed within the server.  The clients will define and manage the relatively small lists of items called ‘groups’ as needed from time to time.  The interfaces described here provide the client the ability to easily define, manage, and recreate these lists as needed through the use of ‘OPCGroups’.  The clients direct the server to create, manage and delete these groups on their behalf (persistence of the groups is the responsibility of the client application). Although it is possible, with the usage of public groups, that the server could provide persistent storage of these type of groups, or treat them as server defined groups.

## Local vs. Remote Servers

It is expected that OPC Server vendors will take one of two approaches to networking:

- They can indicate that the client should always connect to a local server which makes use of an existing proprietary network scheme.  In this case the ‘node’ of the data might be specified as part of the OPC Item Definition.  This approach will commonly be used by vendors who are adding OPC capability to an existing distributed product.

- They can indicate the client should connect to the desired server on the target node and make use of DCOM™ to provide networking.  For this reason all of the RPC_E_* error codes should also be considered as possible returns from the functions below.

## Application Level Server and Network Node Selection

OPC supports the concept of organizing client requests into groups within a server.  Such groups can contain requests for data from only one particular OPC Server object. In order to access data, a client application will need to specify the following:

- The name of the OPC ActiveX™ server (for use by CoCreateInstance, CoCreateInstanceEx, etc.)

- The name of the machine hosting the OPC ActiveX™ server (for use by CoCreateInstanceEx)

- The vendor specific OPC Item Definition (the name of the specific data item in the server’s address space)

It is beyond the scope of this specification to discuss the implications of this on the architecture and user interface of the client program.

## UNICODE, NT and WIN95

All string parameters to the OPC Interfaces are UNICODE, because the native OLE APIs are all UNICODE.  Microsoft Visual Basic 4.0 is UNICODE internally and, while it normally converts strings to ANSI when calling a DLL, it will pass strings directly as UNICODE where a corresponding TYPELIB indicates this should be done (as it will for OPC).  See also VB4DLL.TXT supplied by Microsoft with the Visual Basic product.

At the time of this writing, MIDL 3.0 or later is required in order to correctly compile the IDL code and generate proxy/stub software. Microsoft Windows NT 4.0 (or later), or Windows 95 with DCOM support is required to properly handle the marshaling of OPC parameters.

Note that in order to implement OPC servers which will run on both Microsoft Windows NT and Microsoft Windows 95 it is necessary for these servers to test the platform at runtime. In the case of Microsoft Windows 95, conversion of  any strings to be passed to Win32 from UNICODE to ANSI needs to be done.

## Threads and Multitasking

This specification does NOT require any particular threading model for the server.

The topic of multiple threads and their relationship to OLE is important.  While these issues are also difficult to summarize, the performance gains for a medium to large scale server are worth the investment.

For OPC Servers

For servers, the default handling of threads by OLE is very simplistic.  OLE will use one thread per local or remote server to handle all requests for all clients.  An alternate approach is referred to ‘Apartment Model Threading’ where all OLE calls into an OLE server are guaranteed to be serialized.  The apartment model simplifies the issues surrounding. multiple client access.

An advantage to this single threaded approach is that it simplifies implementation of servers with respect to reentrancy issues.  Since all method calls are serialized automatically by the message loop, methods are never reentered or interrupted by other methods.  Another advantage is that it insures (as required by COM) that all access to an object is done by the thread that created the object.

The major disadvantage of this single threaded approach is that all method calls must run to completion without significant delay.  Any delay by a call prevents execution of the message loop and dispatch of additional requests, thus blocking all clients of the server.  This means that a data read or write will need to be buffered so as not to seriously compromise speed.  In particular, this means that physical communications (unless they are very fast) should be handled by a separate thread within the server (clearly logic related to data handling by this thread would need to be thread safe).  This in turn makes write verification and error handling for writes more difficult.  These issues are reflected in the design of the interfaces, particularly in the areas of ‘allowed behavior’.  It will be noted later that the design allows for optional Read and Write modes where the data is read or written directly to the device.

For OPC Clients

It is currently a requirement of COM that an object be accessed only by the thread that created it.  This applies both to the actual objects in the server and to any ‘proxy’ objects represented by a marshaling stub or handler.  Note that there are ways to partially relax this constraint (e.g. through the use of CoMarshallInterThreadInterfaceInStream()) however,this simply routes all method calls back through the thread that created the object and this involves considerable overhead.  In addition, no matter how many threads attempt to access the objects in parallel, they will all be gated by the operation of the dispatch loop in the thread owning the object which will tend to negate any performance improvement.

Note the general OLE rule that code within asynchronous OLE methods (e.g. OnDataChange) cannot make synchronous or asynchronous OLE calls.

## Synchronization and Serialization Issues

By ‘synchronization’ we mean the ability of a client to read or write values and attributes in a single transaction.  For example, most applications want to insure that the value, quality and time stamp attributes of a particular item are in ‘sync’.  Also, a reporting package might want to insure that a group of several values read together as part of a ‘Batch Report’ are in fact part of the same batch.  Finally, a recipe download package would want to insure that all of the values in the group were sent together and that the recipe was not started until all of the values had been received.  These are just a few examples where synchronization is important.

The short answer is that OPC itself cannot insure that all of these synchronization tasks can be accomplished.  Additional handshaking and flag passing between the client application and the device server to signal such states as ‘ready’ and ‘complete’ will be required.  There are also things that need to be specified about the behavior of OPC servers to assure that OPC does not prevent this sort of synchronization from being done.

It will be seen later that OPC allows explicit reads and writes of groups of items or of individual items as well as exception based data connections (OnDataChange).  Without jumping ahead too far it is possible to make some general observations about these issues and about server behavior.

- In general, OPC Servers should try to preserve synchronization of data items and attributes that are read or written in a single operation.  Synchronization of items read or written individually in separate operations is not required.  Clearly, data read from different physical devices is difficult to synchronize.

- Reads and writes of data items which can be accessed by more than one thread must be implemented to be thread safe, to the extent that data synchronization is preserved as specified in this specification.  Examples of where this is important might include: logic within a server where one thread services method executions while a separate thread performs the physical communications and writes the received data into a buffer area which is shared with the first thread.  Another example might be the logic in a handler or proxy where a ‘hidden’ RPC thread servicing an OnDataChange subscription is writing data into a shared buffer which a thread in the client might be reading.

- Threading issues are always important but this is especially true on SMP systems.

By ‘Serialization’ we mean the ability of the client to control the order in which writes are performed.

- It is STRONGLY RECOMMENDED that write requests to the same device be handled ‘in-order’ by any server implementation.  For example, an application might use a ‘recipe download complete’ flag which is set by the application after the individual recipe items are sent.  In this case, the data must be transmitted to the physical device in the same order it was output to insure that the ‘complete’ flag is not set before all the data has actually arrived. Where the server buffers the outgoing data and implements a separate communications manager thread to send these outputs to the physical device (as is often the case), the server implementation must take extra care to insure that the order of the outputs is preserved.

- Where a client can both read values explicitly or receive updates via a callback attention must be given to defining exactly when a callback will or will not occur.  This is discussed in more detail later.

Many of these issues will be clarified in the detailed descriptions of the methods below.

## Public (aka shared) Groups

The purpose of the public group concept is to provide a way to share data configuration information across multiple client applications. Typically, in process control systems, multiple client applications are configured to monitor or control the same process control data using the same applications or tools.   A public group can be created, such that only one application / end-user defines the items, and other client applications access the information in the public group by connecting to it.  This facilitates keeping the definitions of the same data in sync, since only one client has to create and configure the attributes of the data items.

Because the information is shared across multiple clients, some restrictions may be required to make sure that the configuration information across multiple clients remains consistent.

## Persistent  Storage Story

OPC Servers may implement an optional interface to facilitate OPC clients telling an OPC server to persistent (store) the OPC server configuration information.  OPC Server configuration information may include information about the devices and data source necessary to facilitate communication between the data source and the OPC server.  Client configuration information, including the groups and items are not persistently stored by an opc server.

Clients are responsible for the configuration and persistent storage of the groups and items that are required by their application..

# OPC Quick Reference

This section includes a quick reference for the methods on the Custom interfaces and the methods and properties of the Automation Interface. These interfaces, their parameters and behavior are defined in more detail later in the reference sections.

## Custom Interface

Note: This section does not show additional standard enumerators used by this interface.

OPCServer

IOPCServer

IOPCServerPublicGroups (optional)

IOPCBrowseServerAddressSpace (optional)

IPersistFile (optional)

OPCGroup

IOPCGroupStateMgt

IOPCPublicGroupStateMgt (optional)

IOPCSyncIO

IOPCAsyncIO

IOPCItemMgt

IDataObject

EnumOPCItemAttributes

IEnumOPCItemAttributes

### OPCServer Object

IOPCServer

| HRESULT | AddGroup(szName, bActive, dwRequestedUpdateRate, hClientGroup, pTimeBias, pPercentDeadband, dwLCID, phServerGroup, pRevisedUpdateRate, riid, ppUnk) |
| --- | --- |
| HRESULT | GetErrorString(dwError, dwLocale, ppString) |
| HRESULT | GetGroupByName(szName, riid, ppUnk) |
| HRESULT | GetStatus(ppServerStatus) |
| HRESULT | RemoveGroup(hServerGroup, bForce) |
| HRESULT | CreateGroupEnumerator(dwScope, riid, ppUnk) |

IOPCServerPublicGroups (optional)

| HRESULT | GetPublicGroupByName(szName, riid, ppUnk); |
| --- | --- |
| HRESULT | RemovePublicGroup(hServerGroup, bForce); |

IOPCBrowseServerAddressSpace (optional)

| HRESULT | QueryOrganization(pNameSpaceType ); |
| --- | --- |
| HRESULT | ChangeBrowsePosition(dwBrowseDirection, szString ); |
| HRESULT | BrowseOPCItemIDs( dwBrowseFilterType, szFilterCriteria, vtDataTypeFilter, dwAccessRightsFilter, ppIEnumString ); |
| HRESULT | GetItemID( szItemDataID, szItemID ); |
| HRESULT | BrowseAccessPaths( szItemID, ppIEnumString ); |

IPersistFile (optional)

| HRESULT | IsDirty(); |
| --- | --- |
| HRESULT | Load(pszFileName, dwMode); |
| HRESULT | Save(pszFileName, fRemember); |
| HRESULT | SaveCompleted( pszFileName); |
| HRESULT | GetCurFileName( ppszFileName); |

### OPCGroup Object

IOPCGroupStateMgt

| HRESULT | GetState(pUpdateRate, pActive, ppName, pTimeBias, pPercentDeadband, pLCID, phClientGroup, phServerGroup) |
| --- | --- |
| HRESULT | SetState(pRequestedUpdateRate, pRevisedUpdateRate, pActive, pTimeBias, pPercentDeadband, pLCID, phClientGroup) |
| HRESULT | SetName(szName); |
| HRESULT | CloneGroup(szName, riid, ppUnk); |

IOPCPublicGroupStateMgt (optional)

| HRESULT | GetState(pPublic); |
| --- | --- |
| HRESULT | MoveToPublic(void); |

IOPCSyncIO

| HRESULT | Read(dwSource, dwNumItems, phServer, ppItemValues, ppErrors) |
| --- | --- |
| HRESULT | Write(dwNumItems, phServer, pItemValues, ppErrors) |

IOPCAsyncIO

| HRESULT | Read(dwConnection, dwSource, dwNumItems, phServer, pTransactionID, ppErrors,) |
| --- | --- |
| HRESULT | Write(dwConnection, dwNumItems, phServer, pItemValues, pTransactionID, ppErrors); |
| HRESULT | Cancel (dwTransactionID); |
| HRESULT | Refresh(dwConnection, dwSource, pTransactionID); |

IOPCItemMgt

| HRESULT | AddItems(dwNumItems, pItemArray, ppAddResults, ppErrors) |
| --- | --- |
| HRESULT | ValidateItems(dwNumItems, pItemArray, bBlobUpdate, ppValidationResults, ppErrors) |
| HRESULT | RemoveItems(dwNumItems, phServer, ppErrors) |
| HRESULT | SetActiveState(dwNumItems, phServer, bActive, ppErrors) |
| HRESULT | SetClientHandles(dwNumItems, phServer, phClient, ppErrors) |
| HRESULT | SetDatatypes(dwNumItems, phServer, pRequestedDatatypes, ppErrors) |
| HRESULT | CreateEnumerator(riid, ppUnk) |

IDataObject

| HRESULT | DAdvise(pFmt, adv, pSnk, pConnection); |
| --- | --- |
| HRESULT | DUnadvise(Connection); |

Note: all other functions can be stubs which return E_NOTIMPL.

### EnumOPCItemAttributes Object

IEnumOPCItemAttributes

| HRESULT | Next(celt, ppItemArray, pceltFetched); |
| --- | --- |
| HRESULT | Skip(celt); |
| HRESULT | Reset( void); |
| HRESULT | Clone(ppEnumItemAttributes); |

## Custom Interface/Client Side

IAdviseSink (Client side)

| HRESULT | OnDataChange(pFE, pSTM); |
| --- | --- |

Note: all other functions can be stubs which return E_NOTIMPL.

## Automation Interface

OPCServer

IOPCServerDisp

IOPCServerPublicGroupsDisp (optional)

IOPCBrowseServerAddressSpaceDisp (optional)

OPCGroup

IOPCItemMgtDisp

IOPCGroupStateMgtDisp

IOPCSyncIODisp

IOPCAsyncIODisp

IOPCPublicGroupStateMgtDisp (optional)

OPCItem

IOPCItemDisp

### OPCServer Object

IOPCServerDisp

| Properties |  |
| --- | --- |
| Long | Count |
| Object | _NewEnum |
| DATE | StartTime |
| DATE | CurrentTime |
| DATE | lastUpdateTime |
| Short | MajorVersion |
| Short | MinorVersion |
| Short | BuildNumber |
| STRING | VendorInfo |

| Methods |  |
| --- | --- |
| Object | Item(Item) |
| Object | AddGroup(Name, Active, ReqestedUpdateRate, ClientGroupHandle, pPercentDeadband, LCID, pServerGroupHandle, RevisedUpdateRate, pTimeBias) |
| String | GetErrorString( Error, Locale ) |
| Object | GetGroupByName( Name ) |
|  | RemoveGroup(ServerGroupHandle, Force) |
|  | SaveConfig(FileName) |
|  | LoadConfig(FileName) |
|  | SetEnumeratorType(Scope, Type) |

IOPCServerPublicGroupsDisp (optional)

| Methods |  |
| --- | --- |
| Object | GetPublicGroupByName( Name ) |
|  | RemovePublicGroup(ServerGroupHandle, Force) |

IOPCBrowseServerAddressSpaceDisp (optional)

| Properties |  |
| --- | --- |
| Object | _NewEnum |
| Long | Organization |

| Methods |  |
| --- | --- |
|  | ChangeBrowsePosition(BrowseDirection, Position) |
|  | SetItemIDEnumerator(BrowseFilterType, FilterCriteria, DataTypeFilter, AccessRightsFilter) |
| String | GetItemIDString(ItemDataID) |
|  | SetAccessPathEnumerator(ItemID) |

### OPCGroup Object

IOPCItemMgtDisp

| Properties |  |
| --- | --- |
| Long | Count |
| Object | _NewEnum |

| Methods |  |
| --- | --- |
| Object | Item(ItemSpecifier) |
|  | AddItems(NumItems, ItemIDs, ActiveStates, ClientHandles, pServerHandles, pErrors, pItemObjects, [AccessPaths], [RequestedDataTypes], [pBlobs], [pCanonicalDataTypes], [pAccessRights]) |
|  | ValidateItems(NumItems, ItemIDs, pErrors, [AccessPaths], [RequestedDataTypes], [BlobUpdate], [pBlobs], [pCanonicalDataTypes], [pAccessRights]) |
|  | RemoveItems(NumItems, ServerHandles, pErrors, Force) |
|  | SetActiveState(NumItems, ServerHandles, ActiveState, pErrors) |
|  | SetClientHandles(NumItems, ServerHandles, ClientHandles, pErrors) |
|  | SetDatatypes(NumItems, ServerHandles, RequestedDataTypes, pErrors) |

IOPCGroupStateMgtDisp

| Properties |  |
| --- | --- |
| BOOLEAN | ActiveStatus |
| LONG | ClientGroupHandle |
| LONG | ServerGroupHandle |
| STRING | Name |
| LONG | UpdateRate |
| LONG | TimeBias |
| LONG | PercentDeadBand |
| LONG | LCID |

| Methods |  |
| --- | --- |
| Object | CloneGroup([Name]) |

IOPCSyncIODisp

| Properties |  |
| --- | --- |

| Methods |  |
| --- | --- |
| Object | OPCRead(Source, NumItems, ServerHandles, pValues, [pQualities], [pTimestamps], [pErrors]) |
| Object | OPCWrite (NumItems, ServerHandles, Values, [pErrors]) |

IOPCASyncIODisp

| Properties |  |
| --- | --- |

| Methods |  |
| --- | --- |
| Long | AddCallbackReference(Context, pCallback) |
|  | DropCallbackReference(Connection) |
| Long | OPCRead(Source, NumItems, ServerHandles, [pErrors]) |
| Long | OPCWrite (NumItems, ServerHandles, Values, [pErrors]) |
|  | Cancel(TransactionID) |
| Long | Refresh (Source) |

IOPCPublicGroupStateMgtDisp

| Properties |  |
| --- | --- |
| BOOLEAN | State |

| Methods |  |
| --- | --- |
|  | MoveToPublic() |

### OPCItem Object

IOPCItemDisp

| Properties |  |
| --- | --- |
| String | AccessPath |
| LONG | AccessRights |
| BOOLEAN | ActiveStatus |
| VARIANT | Blob |
| LONG | ClientHandle |
| String | ItemID |
| LONG | ServerHandle |
| Short | RequestedDataType |
| VARIANT | Value |
| SHORT | Quality |
| DATE | TimeStamp |
| LONG | ReadError |
| Short | EUType |
| VARIANT | EUInfo |
| LONG | WriteError |

| Methods |  |
| --- | --- |
|  | OPCRead(Source, pValue, [pQuality], [pTimeStamp]) |
|  | OPCWrite(NewValue) |

## Automation Interface/Client Side

Sub OnDataChange( GroupHandle as Long, Count as Long, ClientHandles() as Long,

Values() as Variant, Qualities() as Long, GroupTime as Date,

TimeStamps() as Date )

Sub OnAsyncWriteComplete( GroupHandle as Long, Count as Long, CallbackHandles() as Long,

ItemResults() as Long )

# OPC Custom Interface

## Overview of the OPC Custom Interface

The OPC Custom Interface Objects include the following custom objects:

- OPCServer

- OPCGroup

The interfaces and behaviors of these objects are described in detail in this chapter.   Developers of OPC servers are required to implement the OPC objects by providing the functionality defined in this chapter.

This chapter also references and defines expected behavior for the standard OLE interfaces. Interfaces that an OPC server and an OPC client are required to implement when building OPC compliant components.

Also, standard and custom Enumerator objects are created, and interfaces to these objects are returned. In general the enumerator objects and interfaces are described briefly since their behavior is well defined by OLE.

The OPC specification follows the preferred approach that enumerators are created and returned from methods on objects rather than through QueryInterface. The enumerators are as follows:

- Group Enumerator - (see IOPCServer::GreateGroupEnumerator)

- Item Attribute Enumerator - (see IOPCItemMgt::CreateEnumerator)

- Server Address Space Enumerator - (see IOPCBrowseServerAddressSpace::BrowseOPCItemIDs)

- AccessPath Enumerator - (see IOPCBrowseServerAddressSpace::BrowseAccessPaths)

## General Information

This section provides general information about the OPC Interfaces, and some background information about how the designers of OPC expected these interfaces to be implemented and used.

### Ownership of memory

Per the COM specification, clients must free all memory associated with ‘out’ or ‘in/out’ parameters.  This includes memory that is pointed to by elements within any structures.  This is very important for client writers to understand, otherwise they will experience memory leaks that are difficult to find.  See the IDL file to determine which parameters are out parameters.  The recommended approach is for a client to create a subroutine that is  used for freeing each type of structure properly.

Independent of success/failure, the server must always return well defined values for ‘out’ parameters. Releasing the allocated resources is the client’s responsibility.

Note:  If the error result is any FAILED error such as E_OUTOFMEMORY , the OPC server should return NULL for all `out' pointers (this is standard COM behavior).  This rule also applies to the error arrays (ppErrors) returned by many of the functions below.  In general, a robust OPC client should check each out or in/out pointer for NULL prior to freeing it.

### Standard Interfaces

Per the COM specification, all methods must be implemented on each required interface. Methods which are not required can return E_NOTIMPL or  S_OK depending on the situation.  Any optional interfaces that are supported must have all functions within that interface implemented, even if the implementation is only a stub implementation returning E_NOTIMPL.

### Null Strings and Null Pointers

Both of these terms are used below.  They are NOT the same thing.  A NULL Pointer is an invalid pointer (0) which will cause an exception if used.  A NULL String is a valid (non zero) pointer to a 1 character array where that character is a NULL (i.e. 0).

### Returned Arrays

You will note the syntax size_is(,dwCount) in the IDL used in combination with pointers to pointers.  This indicates that the returned item is a pointer to an actual array of the indicated type, rather than a pointer to an array of pointers to items of the indicated type.  This simplifies marshaling , creation, and access of the data by the server and client.

### Public Groups

Public groups are optional. The server vendor and the client vendor may elect to support this behavior as appropriate for their application.  There are some specific rules that must be adhered to if the public group capability is supported. This are discussed in detail later in the method descriptions but in general:

A public group must have a unique name relative to all other public groups.  If a client adds a private group which will later be converted to a public group, the client should insure that this name is unique or an error will occur later in MoveToPublic.

Once a group has been made public, the items within that group can not be changed.  If changes need to be made to a public group, a new group must be created with the items (e.g. through the use of CloneGroup), and made public after the modifications to the items are in place

Once a client has connected to a public group, most of that group’ properties (client handles, update rates, etc) will be maintained as unique instance data for that client to group connection.

### CACHE data and DEVICE data

For the most part the terms CACHE and DEVICE are treated as ‘abstract’ within this specification. That is, reading CACHE or DEVICE data simply affects the described behavior of various interfaces in a well defined way. The implementation details of these capabilities is not dictated by this specification.

In practice, however, it is expected that most servers will read data into some sort of CACHE. Also, most clients will read data from this cache via one of several mechanisms discussed later. Access to DEVICE data is expected to be ‘slow’ and is expected to be used primarily for diagnostics or for particularly critical operations.

The CACHE should reflect the latest value of the data (subject to update rate and deadband optimizations as discussed later) as well as the quality and timestamp. The Timestamp should indicate the time that the value and quality was obtained by the device (if this is available) or the time the server entered the value and quality into it’s CACHE.

### Asynchronous vs. Synchronous Interfaces

Assuming that most clients want to access Cached data, there are several ways for a client to obtain that data from a server.

- It can perform a synchronous read from cache (simple and reasonably efficient). This may be appropriate for fairly simple clients which are reading relatively small amounts of data and where maximum efficiency is not a concern.  that a client that operates in this way is essentially duplicating the ‘scanning’ that the server is already doing.

- It can ‘subscribe’ to cached data using IAdviseSink which is more complex but very efficient. This is the recommended behavior for clients because it will minimize use of CPU and NETWORK resources.

- It can perform Async reads from cache. However, this is both complex and inefficient. Async reads are intended primarily for use with DEVICE data.

### The ACTIVE flags, Deadband and Update Rate

These attributes of groups and items can be used to reduce resource use by clients and servers. They are discussed in more detail later under GROUPS. In general,  they affect how often the cached data and quality information is updated and how often calls are made to the client’s IAdviseSink.

### Data Acquisition and Active State Behavior

The following table summarizes the expected behavior of OPC servers and OPC clients with respect to the Group and Item Active flags, and CACHE and DEVICE data.

The information in this table is also applicable to the automation interface.

The first column(Function) is the short hand notation for the external functions that an OPC client application calls and the OPC server implements.  The second column (Source) is the source from which the client wants the data to be obtained (either device or cache). The third column (Group) is the active state of the group.. The fourth column (Item) is the active state of the Item. The fifth column(Behavior) is the behavior for this configuration state.

Certain Quality values are identified in the table and reflect required behavior with respect to the active state of groups and items.   In all other cases, the server may return quality values as appropriate to communicate the current state of the data to the client.

| Function | Source | Group | Item | Behavior & Return Codes |
| --- | --- | --- | --- | --- |
| SyncRead | Cache | Active | Active | The cached Values and Quality for the requested items are returned. |
|  | Cache | Active | InActive | The requested items are returned with the quality flag set to OPC_QUALITY_OUT_OF_SERVICE. |
|  | Cache | InActive | Active ¦ InActive | The requested items are returned with the quality flag set to OPC_QUALITY_OUT_OF_SERVICE. |
|  | Device | Active ¦ InActive | Active ¦ InActive | The Values and Quality are obtained by the server from the physical data source and returned to the client. |
| AsyncRead | Cache | Active | Active | The valid cached values for the requested items are sent in the OnDataChange call. |
|  | Cache | Active | InActive | The requested items are sent in the OnDataChange call with the quality flag set to OPC_QUALITY_OUT_OF_SERVICE. |
|  | Cache | InActive | Active ¦ InActive | The requested items are sent in the OnDataChange call with the quality flag set to OPC_QUALITY_OUT_OF_SERVICE. |
|  | Device | Active ¦ InActive | Active ¦ InActive | The Values and Quality are obtained by the server from the physical data source and returned to the client in the OnDataChange call. |
| Refresh | Cache | Active | Active | The cached Values and Qualities for all Active items in the group are sent to the client in the OnDataChange call. |
|  | Cache | Active | InActive | The valid cached Values and Qualities for all Active items in the group are sent to the client in the OnDataChange call. Inactive items are not included. If there are no Active Items in the group then server returns E_FAIL on call. |
|  | Cache | InActive | Active ¦ InActive | Server returns E_FAIL on call. |
|  | Device | Active | Active | First, the Values and Quality are obtained by the server from the physical data source and used to refresh all Active cached values. Then the cached values and qualities for all Active items in the group are sent to the client in the OnDataChange call. (Same as Refresh from Cache) |
|  | Device | Active | InActive | As above. If there are no Active Items in the group then server returns E_FAIL on call. |
|  | Device | InActive | Active ¦ InActive | Server returns E_FAIL on call. |
| Subscription |  | Active | Active | The values and Qualitiy are obtained by the server from the physical data source for the Active items in the group at the requested Update Rate. If the Quality has changed, the new quality and value are stored. Otherwise the current and previous CACHE values are compared using the DeadBand. If the deadband is exceeded then the new value is stored. If the value or quality of the data has changed from the last value provided to the client then the new value and quality are sent to the client in the OnDataChange call. |
|  |  | Active | InActive | Server only acquires values from physical data sources for active items. |
|  |  | InActive | Active ¦ InActive | Server only acquires values from physical data sources for active items that are contained in active groups. |

Additional Notes:

There is a significant difference between the AsyncRead and Subscription services with respect to  a group or item being inactive.  Quality information is returned for inactive items either at the item or the group level for the AsyncRead, where nothing is provided for the subscription services case.

Refresh is a special case of subscription, where refresh forces an OnDataChange call for all active items.

It is expected that most clients will use either Reads or Subscriptions for a particular group but not both. If both are used then there is some interaction between Reads and Subscriptions in that anything sent to the client as a result of a ‘read’ is also considered to be the ‘last value sent’.

A transition from Inactive to Active will result in a change in quality, and will cause a subscription callback for the item or items affected. A change (in the group or item) from Active to Inactive will cause a change in quality but will not cause a callback since by definition callbacks do not occur for inactive items.

### Errors and return codes

The OPC specification describes interfaces and corresponding behavior that an OPC server implements, and an OPC client application depends on.   A list of OPC Specific errors and return codes is contained in the summary of OPC error codes section in this specification.  For each method described below a list of all possible OPC error codes as well as the most common OLE error codes is included. It is likely that clients will encounter additional error codes such as RPC and Security related codes in practice and they should be prepared to deal with them.

In two cases (Read and Write) it is also allowed for a server to return Vendor Specific error codes. Such codes can be passed to GetErrorString method. This is discussed in more detail later.

In all cases  ‘E’ error codes will indicate FAILED type errors and ‘S’ error codes will indicate at least partial success.

## OPCServer Object

### Overview

The OPCServer object is the primary object that an OPC server exposes.  The interfaces that this object provides include:

- IUnknown

- IOPCServer

- IOPCServerPublicGroups (optional)

- IOPCBrowseServerAddressSpace (optional)

- IPersistFile (optional)

The functionality provided by each of the above  interfaces is defined in this section.

NOTE: Version 1.0 of this specification listed IEnumUnkown as an interface on the OPC Server. This was an error and has been removed. The semantics of QueryInterface do not allow such an implementation. The proper way to obtain a group enumerator is through IOPCServer::GreateGroupEnumerator.

### IUnknown

The server must provide a standard IUnknown Interface. Since this is a well defined interface it is not discussed in detail. See the OLE Programmer’s reference for additional information. This interface must be provided, and all  functions implemented as required by Microsoft..

### IOPCServer

This is the main interface to an OPC server.  The OPC server is registered with the operating system as specified in the Installation and Registration Chapter of this specification.

This interface must be provided, and all  functions implemented as specified.

#### IOPCServer::AddGroup

HRESULT AddGroup(

[in, string] LPCWSTR szName,

[in] BOOL bActive,

[in] DWORD dwRequestedUpdateRate,

[in] OPCHANDLE hClientGroup,

[unique, in] LONG *pTimeBias,

[in] FLOAT * pPercentDeadband,

[in] DWORD dwLCID,

[out] OPCHANDLE * phServerGroup,

[out] DWORD *pRevisedUpdateRate,

[in] REFIID riid,

[out, iid_is(riid)] LPUNKNOWN * ppUnk

);

Description

Add a Group to a Server.

| Parameters | Description |
| --- | --- |
| szName | Name of the group. The name must be unique among the other groups created by this client. If no name is provided (szName is NULL) the server will generate a unique name. The server generated name will also be unique relative to any existing public groups. |
| bActive | FALSE if the Group is to be created as inactive. TRUE if the Group is to be created as active. |
| dwRequestedUpdateRate | Client Specifies the fastest rate at which data changes may be sent to OnDataChange for items in this group. This also indicates the desired accuracy of Cached Data. This is intended only to control the behavior of the interface. How the server deals with the update rate and how often it actually polls the hardware internally is an implementation detail. Passing 0 indicates the server should use the fastest practical rate. The rate is specified in milliseconds. |
| hClientGroup | Client provided handle for this group. [refer to description of data types, parameters, and structures for more information about this parameter] |
| pTimeBias | Pointer to Long containing the initial TimeBias for the Group. Pass a NULL Pointer if you wish the group to use the default system TimeBias. |
| pPercentDeadband | The percent change in an item value that will cause n subscription callback for that value to a client. This parameter only applies to items in the group that have dwEUType of Analog. [See discussion of Percent Deadband in Section 4.4.1]. A NULL pointer is equivalent to 0.0. |
| dwLCID | The language to be used by the server when returning values (including EU enumeration’s) as text for operations on this group. This could also include such things as alarm or status conditions or digital contact states. |
| phServerGroup | Place to store the unique server generated handle to the newly created group. The client will use the server provided handle for many of the subsequent functions that the client requests the server to perform on the group. |
| pRevisedUpdateRate | Server specifies the fastest rate at which data changes may be sent to the client for items in this group. Passed pointer may be NULL. If the pointer is valid, the server returns the value it will actually use for the UpdateRate which may differ from the RequestedUpdateRate. In general the server should ‘round up’ the requested rate to the next available supported rate. The rate is specified in milliseconds. Server returns HRESULT of OPC_S_UNSUPPORTEDRATE when server returns a value in revisedUpdateRate that is different than RequestedUpdateRate. |
| riid | The type of interface desired (e.g. IOPCItemMgt) |
| ppUnk | Where to store the returned interface pointer. NULL is returned for any HRESULT other than S_OK. |

Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded. |
| E_FAIL | The operation failed. |
| E_OUTOFMEMORY | Not enough memory |
| E_INVALIDARG | An argument to the function was invalid. |
| OPC_E_DUPLICATENAME | Duplicate name not allowed. |
| OPC_S_UNSUPPORTEDRATE | Server does not support specified rate, server returns the rate that it can support in the revised update rate. |
| E_NOINTERFACE | The interface(riid) asked for is not supported by the server. |

Behavior

A Group is a logical container for a client to organize and manipulate data items.

The server will create a group object, and return a pointer to the interface requested by the client.  If the client requests an optional interface that the server does not support,  the server is expected to return an error indicating the interface is not supported.

The requested update rate / revised update rate behavior should be deterministic between client / server sessions.  The client expects that for the same server configuration or workspace; adding a group with a requested update rate will always result in the same RevisedRate independent of the number of clients or items that have been added.

Comments

After being created, the group will have a reference count of at least 2. One for the ‘Add’ and one for the Interface that was created. The Client must do a Release on the interface when it is done with it. Even if all the interfaces are released,  the group will not be deleted until RemoveGroup is called. See the CreateGroupEnumerator function for additional information.

The level of localization supported (dwLCID) is entirely server specific.  Servers which do not support dynamic localization can ignore this parameter.

See the MoveToPublic function for additional requirements related to public groups.

The default TimeBias for the group will be that of the system in which the group is created.

#### IOPCServer::GetErrorString

HRESULT GetErrorString(

[in] HRESULT dwError,

[in] LCID dwLocale,

[out, string] LPWSTR *ppString

);

Description

Returns the error string for a server specific error code.

| Parameters | Description |
| --- | --- |
| dwError | A server specific error code that the client application had returned from an interface function from the server, and for which the client application is requesting the server’s textual representation. |
| dwLocale | The locale for the returned string . |
| ppString | Pointer to pointer where server supplied result will be saved |

Return Codes

| Return Code | Description |
| --- | --- |
| E_FAIL | The operation failed. |
| E_OUTOFMEMORY | Not enough memory |
| E_INVALIDARG | An argument to the function was invalid. (For example, the error code specified is not valid.) |
| S_OK | The operation succeeded. |

Comments

The expected behavior is that this will include handling of Win32 errors as well (such as RPC errors).

Client must free the returned string.

It is recommended that the server put any OPC specific strings into an external resource to simplify translation.

To get the default value for the system, the dwLocale should be LOCALE_SYS_DEFAULT.

#### IOPCServer::GetGroupByName

HRESULT GetGroupByName(

[in, string] LPCWSTR szName,

[in] REFIID riid,

[out, iid_is(riid)] LPUNKNOWN * ppUnk

);

Description

Given the name of a private group (created earlier by the same client), return an additional interface pointer.  Use GetPublicGroupByName to attach to public groups.

| Parameters | Description |
| --- | --- |
| szName | The name of the group. That is the group must have been created by the caller. |
| riid | The type of interface desired for the group (e.g. IOPCItemMgt) |
| ppUnk | Pointer to where the group interface pointer should be returned. NULL is returned for any HRESULT other than S_OK. |

Return Codes

| Return Code | Description |
| --- | --- |
| E_FAIL | The operation failed. |
| E_OUTOFMEMORY | Not enough memory |
| E_INVALIDARG | An argument to the function was invalid. |
| S_OK | The operation succeeded. |
| E_NOINTERFACE | The interface(riid) asked for is not supported by the server. |

Comments

This function can be used to reconnect to a private group for which all interface pointers have been released.

The client must release the returned interface when it is done with it.

If needed, the client can obtain the hServerGroup Handle via IOPCGroupStateMgt::GetState.

#### IOPCServer::GetStatus

HRESULT GetStatus(

[out] OPCSERVERSTATUS ** ppServerStatus

);

Description

Returns current status information for the server.

| Parameters | Description |
| --- | --- |
| ppServerStatus | Pointer to where the OPCSERVERSTATUS structure pointer should be returned. The structure is allocated by the server. |

Return Codes

| Return Code | Description |
| --- | --- |
| E_FAIL | The operation failed. |
| E_OUTOFMEMORY | Not enough memory |
| E_INVALIDARG | An argument to the function was invalid. |
| S_OK | The operation succeeded. |

Comments

The OPCSERVERSTATUS is described later in this specification.

Client must free the structure as well as the VendorInfo string within the structure.

#### IOPCServer::RemoveGroup

HRESULT RemoveGroup(

[in] OPCHANDLE hServerGroup,

[in] BOOL bForce

);

Description

Deletes the Group

| Parameters | Description |
| --- | --- |
| hServerGroup | Handle for the group to be removed |
| bForce | Forces deletion of the group even if references are outstanding |

Return Codes

| Return Code | Description |
| --- | --- |
| E_FAIL | The operation failed. |
| E_OUTOFMEMORY | Not enough memory |
| E_INVALIDARG | An argument to the function was invalid. |
| S_OK | The operation succeeded. |
| OPC_S_INUSE | Was not be removed because references exist. Group will be marked as deleted, and will be removed automatically by the server when all references to this object are released. |

Comments

A group is not deleted when all the client interfaces are released, since the server itself maintains a reference to the group.  The client may still call  GetGroupByName after all the interfaces have been released. RemoveGroup() causes the server to release it's `last' reference to the group, which results in the group being truly deleted.

In general, a well behaved client will call this function only after releasing all interfaces.

If interfaces still exist, Remove group will mark the group as ‘deleted’.  Any further calls to this group via these interfaces will return E_FAIL. When all the interfaces are released, the group will actually be deleted.  If bForce is TRUE then the group is deleted unconditionally even if references (interfaces) still exist.  Subsequent use of such interfaces will result in an access violation.

This function should not be called for Public Groups.

#### IOPCServer::CreateGroupEnumerator

HRESULT CreateGroupEnumerator(

[in] OPCENUMSCOPE dwScope,

[in] REFIID riid,

[out, iid_is(riid)] LPUNKNOWN* ppUnk

);

Description

Create various enumerators for the groups provided by the Server.

| Parameters | Description |
| --- | --- |
| dwScope | Indicates the class of groups to be enumerated OPC_ENUM_PRIVATE_CONNECTIONS or OPC_ENUM_PRIVATE enumerates all of the private groups created by the client OPC_ENUM_PUBLIC_CONNECTIONS or OPC_ENUM_PUBLIC enumerates all of the public groups available in the server OPC_ENUM_ALL_CONNECTIONS or OPC_ENUM_ALL enumerates all private groups and all public groups |
| riid | The interface requested. This must be IID_IEnumUnknown or IID_IEnumString. |
| ppUnk | Where to return the interface. NULL is returned for any HRESULT other than S_OK. |

NOTE: Version 1.0 of this specification described slightly different behavior for enumerating connected vs non-connected groups. However this behavior has been found to be difficult or impossible to implement in practice. The description here represents a simplification of this behavior. It is recommended that use of OPC_ENUM_PRIVATE_CONNECTIONS, OPC_ENUM_PUBLIC_CONNECTIONS, OPC_ENUM_ALL_CONNECTIONS be avoided by clients.

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| E_FAIL | The operation failed. |
| E_OUTOFMEMORY | Not enough memory |
| E_INVALIDARG | An argument to the function was invalid. |
| S_OK | The operation succeeded. |
| S_FALSE | There is nothing to enumerate (There are no groups that satisfy the request).. |
| E_NOINTERFACE | The interface(riid) asked for is not supported by the server. |

Comments

Connected means an interface pointer exists.

Servers which do not support public groups will simply behave as if they had no public groups.  That is they will NOT return E_INVALIDARG if the scope includes public groups.

IEnumUnknown creates an additional interface pointer to each group in the enumeration (even if the client already has a connection to the group).  If the server has a large number of public groups available then this may involve considerable overhead as well as requiring additional cleanup by the client.  In general, enumerating groups by name will be much faster.

In the case of IEnumUnknown (per the COM specification) the client must also release all of the returned IUnknown pointers when he is done with them.

### IOPCServerPublicGroups (optional)

This optional interface allows management of public groups.

Public Groups

An application may be designed so that the same groups of data items are used by many clients. In those cases the optional Public Group capability of the server provides a convenient mechanism for both clients and servers to share these groups.

Public groups may be created by the server or they may be created by a client.  When created by the client, they are first created as private groups and then converted to public groups by MoveToPublic.

A client can enumerate the available public groups by name using IOPCServer::CreateGroupEnumerator. He can ‘connect’ to a public group by calling GetPublicGroupByName. He can examine the contents of the group via IEnumOPCItemAttributes.  He can assign client handles and datatypes that are meaningful for the particular client using various IOPCItemMgt functions.

Once a client connects to a Public group, it behaves very much like a private group. He can activate and deactivate the group or items in the group. He can set client handles for the group and items within the group. He can set requested data type for the items in the group.  All of these operations affect only that particular client. They do not affect the behavior of other clients connected to that group.  The exception to this behavior is that he cannot add or remove items.

#### IOPCServerPublicGroups:: GetPublicGroupByName

HRESULT GetPublicGroupByName(

[in, string] LPCWSTR szName,

[in] REFIID riid,

[out, iid_is(riid)] LPUNKNOWN * ppUnk

);

Description

‘Connects’ the client to a public group. This returns an interface pointer to the group.

| Parameters | Description |
| --- | --- |
| szName | Name of group to be connected |
| riid | requested interface |
| ppUnk | pointer to place to store interface. NULL is returned for any HRESULT other than S_OK |

Return Codes

| Return Code | Description |
| --- | --- |
| E_FAIL | The operation failed. |
| E_OUTOFMEMORY | Not enough memory |
| E_INVALIDARG | An argument to the function was invalid. |
| S_OK | The operation succeeded. |
| E_NOINTERFACE | The interface(riid) asked for is not supported by the server. |
| OPC_E_NOTFOUND | Requested Public Group was not found. |

Comments

If needed, the client can obtain the hServerGroup Handle via IOPCGroupStateMgt::GetState.

Note that when the client’s last interface for the public group is released, the client is effectively disconnected from the group. At this point the server should release any resources or instance data associated with this particular client’s connection to the public group. It is not necessary for the client to call RemoveGroup or RemovePublicGroup to free these client specific resources.

#### IOPCServerPublicGroups:: RemovePublicGroup

HRESULT RemovePublicGroup(

[in] OPCHANDLE hServerGroup ,

[in] BOOL bForce

);

Description

Delete a public group.

| Parameters | Description |
| --- | --- |
| hServerGroup | Handle of group to be removed. |
| bForce | Forces deletion of the group even if references are outstanding |

Return Codes

| Return Code | Description |
| --- | --- |
| E_FAIL | The operation failed. |
| E_OUTOFMEMORY | Not enough memory |
| E_INVALIDARG | An argument to the function was invalid. |
| S_OK | The operation succeeded. |
| OPC_S_INUSE | Was not be removed because references exist. Group will be marked as deleted, and will be removed by the server when all references to this object are released. |

Comments

A public group is not deleted when all the client interfaces are released, since the server itself maintains a reference to the group.  The client may still call  GetPublicGroupByName after all the interfaces have been released. RemovePublicGroup() causes the server to release it's `last' reference to the group, which results in the group being truly deleted.

It is permissible for a server to publish ‘hard coded’ groups which cannot be deleted. The server should return E_FAIL in this case.

In general, a well behaved client will call this function only after releasing all interfaces.

If interfaces still exist, RemovePublicGroup will mark the group as ‘deleted’.  Any further calls to this group via these interfaces will return E_FAIL. When all the interfaces are released, the group will actually be deleted.  If bForce is TRUE then the group is deleted unconditionally even if references (interfaces) still exist.  Subsequent use of such interfaces will result in an access violation.

Note that any client can delete a public group. You can get the server handle of the group by calling IOPCGroupStateMgt::GetState.

### IOPCBrowseServerAddressSpace (optional)

This interface provides a way for clients to browse the available data items in the server, giving the user a list of the valid definitions for an ITEM ID.  It allows for either flat or hierarchical address spaces and is designed to work well over a network. It also insulates the client from the syntax of a server vendor specific ITEM ID.

Each instance of this interface is a separate object (like an enumerator), which allows multiple independent browse sessions on the server address space.

It is assumed that the underlying server address space is either flat or hierarchical. A flat space will always be presented to the client as Flat. A hierarchical space can be presented to the client as either flat or hierarchical.

A hierarchical presentation of the server address space would behave much like a file system, where the directories are the branches or paths, and the files represent the leaves or items.   For example, a server could present a control system by showing all the control networks, then all of the devices on a selected network, and then all of the classes of data within a device, then all of the data items of that class.  A further breakdown into vendor specific ‘Units’ and ‘Lines’ might be appropriate for a BATCH system.

Note that this functionality is provided as an interface rather than an ActiveX control (a) because an interface is more easily remote and (b) because an interface can more easily be integrated with other browsing methods and address space/configuration tools  that the Client may already provide.

As with any enumerator, when the client obtains this interface, the server creates an object and maintains state information (the current position in the address hierarchy) on behalf of the client.  The server is required to maintain state information for each client that is browsing the address space of the server.  Also, the client cannot perform a query interface from this interface to get back to the server object.

The browse position is initially set to the ‘root’ of the address space.  The client move the browse position within a hierarchical space by calling ChangeBrowsePosition.  For a FLAT space this is ignored

The Client can browse the items below (contained in) the current position via BrowseOPCItemIDs. For a hierarchical space you can specify BRANCH (which returns things on that level with children) or LEAF (things on that level without children)- or FLAT (everything including children of children).  This gives you back a String enumerator.

This browse can also be filtered by a vendor specific filter string, by datatype, or by Access Rights.

In a hierarchy, the enumerator will return ‘short’ strings; the name of the ‘child’.  These short strings will generally not be sufficient for AddItem.  The client should always convert this short string to a ’fully qualified’ string via GetItemID.  For example the short string might be TIC101; the fully qualified string might be AREA1.REACTOR5.TIC101.

This ItemID can optionally be passed to BrowseAccessPaths to get a list of valid access paths to this item. (this returns another string enumerator).

If the client browsed for BRANCHs (things with children) then he can pass the result (short string) to ChangeBrowsePosition to move ‘down’.  This method can also move ‘up’ in which case the short string is not used.

#### IOPCBrowseServerAddressSpace:: QueryOrganization

HRESULT QueryOrganization(

[out] OPCNAMESPACETYPE  * pNameSpaceType

);

Description

Provides a way to determine if the underlying system is inherently flat or hierarchical and how the server may represent the information of the address space to the client.

| Parameters | Description |
| --- | --- |
| pNameSpaceType | Place to put OPCNAMESPACE result which will be OPC_NS_HIERARCHIAL or OPC_NS_FLAT |

Return Codes

| Return Code | Description |
| --- | --- |
| E_FAIL | The operation failed. |
| E_OUTOFMEMORY | Not enough memory |
| E_INVALIDARG | An argument to the function was invalid. |
| S_OK | The operation succeeded. |

Comments

FLAT and HIERARCHICAL spaces behave somewhat different.  If the result is ‘FLAT’ then the client knows that there is no need to pass the BRANCH or LEAF flags to BrowseOPCItemIDs or to call ChangeBrowsePosition

#### IOPCBrowseServerAddressSpace:: ChangeBrowsePosition

HRESULT ChangeBrowsePosition(

[in]  OPCBROWSEDIRECTION dwBrowseDirection,

[in, string] LPCWSTR  szString

);

Description

Provides a way to move ‘up’ or ‘down’ in a hierarchical space.

| Parameters | Description |
| --- | --- |
| dwBrowseDirection | OPC_BROWSE_UP or OPC_BROWSE_DOWN. |
| szString | For DOWN, the name of the branch to move into. This would be one of the strings returned from BrowseOPCItemIDs. For UP this parameter is ignored and should point to a NULL string. |

Return Codes

| Return Code | Description |
| --- | --- |
| E_FAIL | The operation failed. |
| E_OUTOFMEMORY | Not enough memory |
| E_INVALIDARG | An argument to the function was invalid. |
| S_OK | The operation succeeded. |

Comments

The function will return E_FAIL if called for a FLAT space.

An error (E_INVALIDARG) is returned if the passed string does not represent a ‘branch’ (has no children).

An error (E_INVALIDARG)is returned if the caller tries to browse ‘UP’ from the ‘root’.

#### IOPCBrowseServerAddressSpace:: BrowseOPCItemIDs

HRESULT BrowseOPCItemIDs(

[in] OPCBROWSETYPE   dwBrowseFilterType,

[in, string] LPCWSTR  szFilterCriteria,

[in] VARTYPE   vtDataTypeFilter,

[in] DWORD    dwAccessRightsFilter,

[out] LPENUMSTRING  * ppIEnumString

);

Description

Returns an IENUMString for a list of ItemIDs as determined by the passed parameters.  The position from the which the browse is done can be set via ChangeBrowsePosition.

| Parameters | Description |
| --- | --- |
| dwBrowseFilterType | OPC_BRANCH - returns only items that have children OPC_LEAF - returns only items that don’t have children OPC_FLAT - returns everything at and below this level including all children of children - basically ‘pretends’ that the address space in actually FLAT This parameter is ignored for FLAT address space. |
| szFilterCriteria | A server specific filter string. This is entirely free format and may be entered by the user via an EDIT field. The valid criteria is server vendor specific Support for some form of regular expressions (e.g. wild card as ‘*’) is recommended but not required. A NULL string indicates no filtering. |
| vtDataTypeFilter | Filter the returned list based in the available datatypes (those that would succeed if passed to AddItem). VT_EMPTY indicates no filtering. Note: the client may specify mulitple datatypes. |
| dwAccessRightsFilter | Filter based on the AccessRights bit mask (OPC_READABLE or OPC_WRITEABLE). 0 indicates no filtering. |
| ppIEnumString | Where to save the returned interface pointer. NULL if the HRESULT is other than S_OK or S_FALSE |

Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded. |
| S_FALSE | There is nothing to enumerate. (However an Enumerator is still returned and must be released). |
| E_FAIL | The operation failed. |
| E_OUTOFMEMORY | Not enough memory |
| E_INVALIDARG | An argument to the function was invalid. |
| OPC_E_INVALIDFILTER | The filter string was not valid |

Comments

The returned enumerator may have nothing to enumerate if no ItemIDs satisfied the filter constraints. The strings returned by the enumerator represent the BRANCHs and LEAFS contained in the current level.  They do not include any delimiters or ‘parent’ names.  Whenever possible the server should return strings which can be passed directly to AddItems.  However, it is allowed for the Server to return a ‘hint’ string rather than an actual legal Item ID.  For example a PLC with 32000 registers could return a single string of “0 to 31999” rather than return 32,000 individual strings from the enumerator.  For this reason (as well as the fact that browser support is optional) clients should always be prepared to allow manual entry of ITEM ID strings. In the case of ‘hint’ strings, there is no indication given as to whether the returned string will be acceptable by AddItem or ValidateItem

Clients are allowed to get and hold Enumerators for more than one ‘browse position’ at a time.

Changing the browse position will not affect any enumerator the client already has.

The client must Release each Enumerator when he is done with it.

#### IOPCBrowseServerAddressSpace:: GetItemID

HRESULT GetItemID(

[in] LPCWSTR  szItemDataID,

[out, string] LPWSTR * szItemID

);

Description

Provides a way to assemble a ‘fully qualified’ ITEM ID in a hierarchical space.  This is required since at each point one is browsing just the names ‘below’ the current node (e.g. the ‘units’ in a ‘cell’).

| Parameters | Description |
| --- | --- |
| szItemDataID | The name of a BRANCH or LEAF at the current level. |
| szItemID | Where to return the resulting ItemID. |

Return Codes

| Return Code | Description |
| --- | --- |
| E_FAIL | The function failed |
| E_INVALIDARG | An argument to the function was invalid. |
| E_OUTOFMEMORY | Not enough memory |
| S_OK | The function was successful |

Comments

When browsing down from REACTOR5 we might see TIC101, TIC102, etc. It is possible that a server could support hierarchical browsing of an address space that contains globally unique tags.  For example in the case of AREA1.REACTOR5.TIC101, the tag TIC101 might still be globally unique and might therefore be acceptable to AddItem.  This may not always be the case, so the expected behavior is that (a) GetItemID will always return the fully qualified name (AREA1.REACTOR5.TIC101) and that (b) that the server will always accept the fully qualified name in AddItems (even if it does not require it).

This function does not need to be called for a FLAT space.  If it is called, then it will simply return the same string that was passed in.

It is valid to form an ItemID that represents a BRANCH (e.g. AREA1.REACTOR5).  This could happen if you pass a BRANCH (AREA1) rather than a LEAF (TIC101).  The resulting string might fail if passed to AddItem.

The client must free the returned string.

ItemID is the unique ‘key’ to the data, it is considered the ‘what’ or ‘where’ that allows the server to connect to the data source.

#### IOPCBrowseServerAddressSpace:: BrowseAccessPaths

HRESULT BrowseAccessPaths(

[in, string] LPCWSTR   szItemID,

[out] LPENUMSTRING * ppIEnumString

);

Description

Provides a way to browse the available AccessPaths for an ITEM ID.

| Parameters | Description |
| --- | --- |
| szItemID | Fully Qualified ItemID |
| ppIEnumString | Where to save the returned string enumerator. NULL if the HRESULT is other that S_OK. |

Return Codes

| Return Code | Description |
| --- | --- |
| E_FAIL | The function failed |
| E_INVALIDARG | An argument to the function was invalid. |
| S_FALSE | There is nothing to enumerate |
| E_OUTOFMEMORY | Not enough memory |
| E_NOTIMPL | The server does not require or support access paths. |
| S_OK | The function was successful |

Comments

Clients are allowed to get Access Path Enumerators for more than one item at a time.

Changing the browse position will not affect any enumerator the client already has.

The client must Release each Enumerator when he is done with it.

AccessPath is the “how” for the server to get the data specified by the itemID (the what).  The client uses this function to identify the possible access paths for the specified itemID.

### IPersistFile (optional)

This is a standard implementation of the IPersistFile Interface. The descriptions below are brief and describe behavior specific to OPC. Refer to the OLE programmers reference for additional information.

This optional interface allows Clients to load or save a server ‘configuration’.  The reason for providing this interface is to allow a client application to have access to any ‘hooks’ it might need to get the system started or to change the system configuration without requiring the user to start a separate program.

The filename discussed below tells the server where it’s configuration information is located. Filename syntax and semantics is server specific, and may include the  fully qualified path and file name, or may refer to a proprietary database where the server’s configuration is stored. The format and content of the file or database is server specific.

Note that this interface does NOT save any client specific information such as group and item definitions.  Rather, it is a ‘hook’ intended to load or save the server configuration such as a SCADA or DCS database, communications baud rates, PLC station addresses, etc.

#### IPersistFile::IsDirty

HRESULT IsDirty(

void

);

Description

Returns whether or not there have been any configuration changes (by any client) since the last save operation.

Parameters

Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The server has configuration information that has been modified since the last save operation. |
| S_FALSE | The server does not have configuration information that has been modified since the last save operation. |

Comments

The client cannot change any of the configuration of the server address space through a standard OPC interface.  The client uses this function to determine if the configuration has been modified by a server specific configuration tool or by a client using a server specific configuration interface.   This function could be used by the client before shutting the server down to determine if the server’s configuration  needs to be saved.

#### IPersistFile::Load

HRESULT Load(

[in] LPCOLESTR pszFileName,

[in] DWORD dwMode

);

Description

Instructs the server to load the server’s configuration data from the file (pszFileName). The previous configuration (if any) is replaced by the new configuration. OPC servers are assumed to support a single (global) active configuration. That is, a load will affect all other OPC clients which are accessing this server.

The exact effect of doing a load while groups and subscriptions are active is server specific. In general, it is assumed that this will cause some or all of the items in the active groups to disappear from the server address space. Such items would subsequently return a BAD Quality.

| Parameters | Description |
| --- | --- |
| pszFileName | The filename from which the server configuration information is to be loaded. |
| dwMode | Access mode to be used on the file. See ‘Storage Access Mode Flags” in the OLE programmer’s reference for more information. |

Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The server successfully loaded configuration information from the file specified. |
| E_FAIL | The server was unsuccessful in loading the configuration information from the file specified. |
| E_OUTOFMEMORY | Not enough memory to load configuration. |
| OPC_E_INVALIDCONFIGFILE | The server's configuration file is an invalid format. |

Comments

In most cases, an error during load will leave the server without a valid configuration.

A load will cause other clients connected to this server to be effectively disconnected, or the results of the other clients subsequent interactions with the server to be unknown.

#### IPersistFile::Save

HRESULT Save(

[in, unique] LPCOLESTR pszFileName,

[in] BOOL fRemember

);

Description

Save current configuration.

Parameters

| Parameters | Description |
| --- | --- |
| pszFileName | The filename to which the server configuration information is to be saved. |
| fRemember | Determines of the logically associated filename for this configuration should be changed (if TRUE) or not (if FALSE). |

Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The server successfully saved configuration information |
| E_FAIL | The server was unsuccessful in saving the configuration |
| OPC_E_INVALIDCONFIGFILE | The server's configuration file is an invalid format. |

Comments

Save should clear the server’s configuration dirty flag (as returned from IsDirty interface).

#### IPersistFile::SaveCompleted

HRESULT SaveCompleted(

[in, unique] LPCOLESTR pszFileName

);

Description

This function may be implemented as a ‘stub’.

| Parameters | Description |
| --- | --- |
| pszFileName | The filename to which the configuration was previously saved using IPersistFile::Save |

Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | S_OK is always returned |
| OPC_E_INVALIDCONFIGFILE | The server's configuration file is an invalid format. |

Comments

#### IPersistFile::GetCurFile

HRESULT GetCurFile(

[out] LPOLESTR *ppszFileName

);

Description

Instructs the server to return the name associated with the currently loaded configuration.

| Parameters | Description |
| --- | --- |
| ppszFileName | The full filename (if any). |

Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| S_FALSE | There is not filename currently associated with the configuration |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | operation failed |

Comments

This may or may not match the last name passed to Load or Save since there can be other vendor specific tasks that control the server configuration.

The client must free the returned string.

## OPCGroup Object

The OPCGroup object is the object that an OPC server delivers to manage a collection of items.  The interfaces that this object provides includes:

- IUnknown

- IOPCGroupStateMgt

- IOPCPublicGroupStateMgt

- IEnumOPCItemAttributes

- IOPCSyncIO

- IOPCAsyncIO

- IOPCItemMgt

- IDataObject

The functionality provided by each of these interfaces is defined in this section.

This section also identifies the interfaces required to be implemented to support the OLE mechanism for delivering a COM interface.

### General Properties

The OPCGroup has certain general properties and behaviors which affect the operation of  the Interfaces and Methods. These are discussed here in order to minimize duplication.

#### Name

Each group has a name. For private groups the name must be unique among the other private groups that belong to that client. For public groups the name must be unique among all of the public groups. While a client can change the name of a private group, the name of a public group cannot be changed.

A private Group and a public group may have the same name as long as the client is not connected to the public group with the same name.

#### Cached data

The methods below allow the client to specify that some operations can be performed on ‘CACHE’ or ‘DEVICE’ as it is expected that most servers will implement some sort of CACHE.  As discussed earlier,  these terms are simply part of the interface definition.  The way the functions described below behave differs slightly based on which source is specified.  The actual details of the implementation of thus functionality is up to the server vendor.  In most cases, access to CACHE data is expected to be ‘fast’ while access to the ‘DEVICE is expected to be ‘slow’ but more accurate. CACHE data is affected by the Active state of the group and the items in the group while DEVICE data is not. Note again that although we sometimes make suggestions, this specification does not dictate any particular implementation or performance.

#### Active

Groups and Items within Groups have an Active Flag. The active state of the group is maintained separately from the active state of the items. Changing the state of the group does not change the state of the items.

For the most part the Active flag is treated as ‘abstract’ within this specification. The state of these flags affects the described behavior of various interfaces in a well defined way. The implementation details of these capabilities is not dictated by this specification.

In practice it is expected that most servers will make use of this flag to optimize their use of communications and CPU resources. Items and Groups which are not active do not need to be maintained in the CACHE.

It is also expected that clients will simply set and clear active flags of groups and items as a more efficient alternative to adding and removing entire groups and items. For example if an operator display is minimized, its items might be set to inactive.

Refer to the Data Acquisition and Active State Behavior summary earlier in this document for a quick overview of the behavior of a client and server with respect to the active state of a group and items.

OnDataChange within the client's address space can be called whenever any active item data in a active group changes, where “change” is defined as a change in value (from the last value sent to this client), or a change in the Quality of the value. The server can return values and quality flags for those items within the group that changed.(this will be discussed more in later sections)

#### Update Rate

The client can specify an ‘update rate’ for each group. This determines the time between when the exception limit is checked. If the exception limit is exceeded, the CACHE is updated. The server should make a ‘best effort’ to keep the data fresh. This also affects the maximum rate at which notifications will be sent to the IAdvise sink. The server should never send data to a client at a rate faster than the client requests.

The update rate is a ‘request’ from the client. The server should respond with an update rate that is as close as possible to that requested.

#### Time Zone (Time Bias)

In some cases the data may have been collected by a device operating in a time zone other than that of the client. Then it will be useful to know what the time of the device was at the time the data was collected (e.g. to determine what ‘shift’ was on duty at the time). The Time zone Bias provides the information needed to convert the time stamp on the data back to the local time of the device.

This time zone information may rarely be used and the device providing the data may not  know its local time zone, therefore it was not prudent to add this overhead to all data transactions. Instead, the OPCGroup provides a place to store a time zone which can be set and read by the client. The default value for this is the time zone of the host computer. The OPCServer will not make use of this value. It is there only for the convenience of the client.

#### Percent Deadband

Deadband will only apply to items in the group that have a dwEUType of Analog available. If the dwEUType is Analog, then the EU Low and EU High values for the item can be used to calculate the range for the item. This range will be multiplied with the Deadband to generate an exception limit. An exception is determined as follows:

Exception if (absolute value of (last cached value - current value) > pPercentDeadband * (EU High - EU Low) )

If the exception limit is exceeded, then the last cached value is updated with the new value and a notification will be sent to the IAdviseSink (if any). The pPercentDeadband is an optional behavior for the server. If the client does not specify this value on a server that does support the behavior, the default value of 0 (zero) will be assumed, and all value changes will update the CACHE.

The UpdateRate for a group determines time between when a value is checked to see if the exception limit has been exceeded. The PercentDeadband is used to keep noisy signals from updating the client unnecessarily.

#### ClientHandle

This handle will be returned in the data stream to IAdviseSink. This allows the client to identify the group to which the data packet belongs.

It is expected that a client will assign unique value to the client handle if it intends to use any of the asynchronous functions of the OPC interfaces, including IOPCAsyncIO, and IDataObject/IAdviseSink interfaces.

#### Reading and Writing Data

There are four ways to get data into a client. IOPCSyncIO::Read, IOPCAsyncIO::Read, IOPCAsyncIO::Refresh and IDataObject/IAdviseSink. In general the four methods all operate independently without ‘side effects’ on each other.

There are two ways to write data out: IOPCSyncIO::Write, IOPCAsyncIO::AsyncWrite

#### Public Groups

It is required that the server track each client's group properties (update rate, deadband, active status, timezone, lcid) for a public group. For example, if two clients with different LCIDs want data from a public group, they can change the state of the group to reflect their LCID and the server must keep track of both.

### IOPCItemMgt

IOPCItemMgt allows a client to add, remove and control the behavior of items is a group.

#### IOPCItemMgt::AddItems

HRESULT AddItems(

[in] DWORD dwNumItems,

[in, size_is(dwNumItems)] OPCITEMDEF * pItemArray,

[out, size_is(,dwNumItems)] OPCITEMRESULT ** ppAddResults,

[out, size_is(,dwNumItems)] HRESULT ** ppErrors

);

Description

Add one or more items to a  group.

| Parameters | Description |
| --- | --- |
| dwNumItems | The number if items to be added |
| pItemArray | Array of OPCITEMDEFs. These tell the server everything it needs to know about the item including the access path, definition and requested datatype |
| ppAddResults | Array of OPCITEMRESULTs. This tells the client additional information about the item including the server assigned item handle and the canonical datatype. |
| ppErrors | Array of HRESULTs. This tells the client which of the items was successfully added. For any item which failed it provides a reason. |

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| E_FAIL | The operation failed. |
| E_OUTOFMEMORY | Not enough memory |
| E_INVALIDARG | An argument to the function was invalid. |
| S_OK | The operation succeeded. |
| S_FALSE | The operation completed with partial success. Refer to individual error returns for failure analysis. |
| OPC_E_PUBLIC | Cannot add items to a public group |

ppErrors Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The function was successful for this item. |
| OPC_E_INVALIDITEMID | The item id is not syntactically valid |
| OPC_E_UNKNOWNITEMID | The item id is not in the server address space |
| OPC_E_BADTYPE | The requested data type cannot be returned for this item (See comment) |
| E_FAIL | The function was unsuccessful. |
| OPC_E_UNKNOWNPATH | The item's access path is not known to the server. |

Comments

It is acceptable to add the same item to the group more than once. This will generate a 2nd item with a unique ServerHandle.

Any FAILED code in ppErrors indicates that the corresponding item was NOT added to the group and that the corresponding OPCITEMRESULT will not contain useful information.

As an alternative to OPC_E_BADTPYE it is acceptable for the server to return any FAILED error returned by VariantChangeType or VariantChangeTypeEx.

The server provided item handle will be unique within the group, but may not be unique across groups. The server is allowed to ‘reuse’ the handles of deleted items.

Items cannot be added to public groups.

The client needs to free all of the memory associated with the OPCITEMRESULTs including the BLOB.

If the server supports the BLOB it will return an updated BLOB in the OPCITEMRESULTs.  This BLOB may differ in both content and size from the one passed by the client in OPCITEMDEF.

Note that if an Advise is active, the client will begin receiving callbacks for active items. This can occur very quickly, perhaps even before the client has time to process the returned results. The client must be designed to deal with this. One simple solution is for the client to clear the Active state of the group while doing AddItems and to restore it after the AddItems is completed and the results are processed.

#### IOPCItemMgt::ValidateItems

HRESULT ValidateItems(

[in] DWORD dwNumItems,

[in, size_is(dwNumItems)] OPCITEMDEF * pItemArray,

[in] BOOL bBlobUpdate,

[out, size_is(,dwNumItems)] OPCITEMRESULT ** ppValidationResults,

[out, size_is(,dwNumItems)] HRESULT ** ppErrors

);

Description

Determines if an item is valid (could it be added without error). Also returns information about the item such as canonical datatype. Does not affect the group in any way.

| Parameters | Description |
| --- | --- |
| dwNumItems | The number if items to be validated |
| pItemArray | Array of OPCITEMDEFs. These tell the server everything it needs to know about the item including the access path, definition and requested datatype |
| bBlobUpdate | If non-zero (and the server supports Blobs) the server should return updated Blobs in OPCITEMRESULTs. If zero (False) the server will not return Blobs in OPCITEMRESULTs. |
| ppValidationResults | Array of OPCITEMRESULTs. This tells the client additional information about the item including the canonical datatype. |
| ppErrors | Array of HRESULTs. This tells the client which of the items was successfully validated. For any item which failed it provides a reason. |

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| E_FAIL | The operation failed. |
| E_OUTOFMEMORY | Not enough memory |
| E_INVALIDARG | An argument to the function was invalid. |
| S_OK | The operation succeeded. |
| S_FALSE | The operation completed with partial success. Refer to individual error returns for failure analysis. |

ppErrors Codes

| Return Code | Description |
| --- | --- |
| S_OK | The function was successful for this item. |
| OPC_E_INVALIDITEMID | The item id is not syntactically valid |
| OPC_E_UNKNOWNITEMID | The item id is not in the server address space |
| OPC_E_BADTYPE | The requested data type cannot be returned for this item (See comment) |
| E_FAIL | The function was unsuccessful for this item. |
| OPC_E_UNKNOWNPATH | The item's access path is not known to the server. |

Comments

The client needs to free all of the memory associated with the OPCITEMRESULTs including the BLOB.

As an alternative to OPC_E_BADTPYE it is acceptable for the server to return any FAILED error returned by VariantChangeType or VariantChangeTypeEx.

#### IOPCItemMgt::RemoveItems

HRESULT RemoveItems(

[in] DWORD dwNumItems,

[in, size_is(dwNumItems)] OPCHANDLE * phServer,

[out, size_is(,dwNumItems)] HRESULT ** ppErrors

);

Description

Removes (deletes) items from a group. Basically this is the reverse of AddItems.

| Parameters | Description |
| --- | --- |
| dwNumItems | Number of items to be removed |
| phServer | Array of server items handles. These were returned from AddItem. |
| ppErrors | Array of HRESULTs. Indicates which items were successfully removed. |

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The function was successful. |
| S_FALSE | The function was partially successful. See the ppErrors to determine what happened |
| E_FAIL | The function was unsuccessful. |
| OPC_E_PUBLIC | Cannot remove items from a public group |

ppError Codes

| Return Code | Description |
| --- | --- |
| S_OK | The corresponding item was removed. |
| OPC_E_INVALIDHANDLE | The corresponding Item handle was invalid. |

Comments

Adding and removing items from a group does not affect the address space of the server or physical device. It simply indicates whether or not the client is interested in those particular items.

Items are not really objects in the custom interface (do not have interfaces), and there is no concept of a reference count for items. The client should insure that no further references are made to deleted items.

Items cannot be removed from a public group.

#### IOPCItemMgt::SetActiveState

HRESULT SetActiveState(

[in] DWORD dwNumItems,

[in, size_is(dwNumItems)] OPCHANDLE * phServer,

[in] BOOL bActive,

[out, size_is(,dwNumItems)] HRESULT ** ppErrors

);

Description

Sets one or more items in a group to active or inactive. This controls whether or not valid data can be obtained from Read CACHE for those items and whether or not they are included in the IAdvise subscription to the group.

| Parameters | Description |
| --- | --- |
| dwNumItems | The number of items to be affected |
| phServer | Array of Server items handles. |
| bActive | TRUE if items are to be activated. FALSE if items are to be deactivated. |
| ppErrors | Array of HRESULTs. Indicates which items were successfully affected. |

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The function was successful. |
| S_FALSE | The function was partially successful. See the ppErrors to determine what happened |
| E_FAIL | The function was unsuccessful. |

ppError Codes

| Return Code | Description |
| --- | --- |
| S_OK | The function was successful. |
| OPC_E_INVALIDHANDLE | The corresponding Item handle was invalid. |

Comments

Deactivating items will not result in a callback (since by definition callbacks do not occur for inactive items).  Activating items will generally result in an IAdvise callback at the next UpdateRate period.

#### IOPCItemMgt::SetClientHandles

HRESULT SetClientHandles(

[in] DWORD dwNumItems,

[in, size_is(dwNumItems)] OPCHANDLE * phServer,

[in, size_is(dwNumItems)] OPCHANDLE * phClient,

[out, size_is(,dwNumItems)] HRESULT ** ppErrors

);

Description

Changes the client handle for one or more items in a group.

| Parameters | Description |
| --- | --- |
| dwNumItems | The number of items to be affected |
| phServer | Array of Server items handles. |
| phClient | Array of new Client item handles to be stored. The Client handles do not need to be unique. |
| ppErrors | Array of HRESULTs. Indicates which items were successfully affected. |

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The function was successful. |
| S_FALSE | The function was partially successful. See the itemResults to determine what happened |
| E_FAIL | The function was unsuccessful. |

itemResults Codes

| Return Code | Description |
| --- | --- |
| S_OK | The function was successful. |
| OPC_E_INVALIDHANDLE | The corresponding Item handle was invalid. |

Comments

In general, it is expected that clients will set the client handle when the item is added and not change it later. This function is most useful for setting the client handles for items in a public group to which the client has connected.

#### IOPCItemMgt::SetDatatypes

HRESULT SetDatatypes(

[in] DWORD dwNumItems,

[in, size_is(dwNumItems)] OPCHANDLE * phServer,

[in, size_is(dwNumItems)] VARTYPE * pRequestedDatatypes,

[out, size_is(,dwNumItems)] HRESULT ** ppErrors

);

Description

Changes the requested data type for one or more items in a group.

| Parameters | Description |
| --- | --- |
| dwNumItems | The number of items to be affected |
| phServer | Array of Server items handles. |
| pRequestedDatatypes | Array of new Requested Datatypes to be stored. |
| ppErrors | Array of HRESULT’s. Indicates which items were successfully affected. |

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The function was successful. |
| S_FALSE | The function was partially successful. See the itemResults to determine what happened |
| E_FAIL | The function was unsuccessful. |

itemResults Codes

| Return Code | Description |
| --- | --- |
| S_OK | The function was successful. |
| OPC_E_INVALIDHANDLE | The corresponding Item handle was invalid. |
| OPC_E_BADTYPE | The requested datatype cannot be supported for this item. (See comment). The previous requested type is left unchanged. |

Comments

In general, it is expected that clients will set the requested datatype when the item is added and not change it later. This function is most useful for setting the datatype for items in a public group to which the client has connected.

As an alternative to OPC_E_BADTPYE it is acceptable for the server to return any FAILED error returned by VariantChangeType or VariantChangeTypeEx.

#### IOPCItemMgt::CreateEnumerator

HRESULT CreateEnumerator(

[in] REFIID riid,

[out, iid_is(riid)] LPUNKNOWN* ppUnk

);

Description

Create an enumerator for the items in the group.

| Parameters | Description |
| --- | --- |
| riid | The interface requested. Normally this is IID_IEnumOPCItemAttributes. |
| ppUnk | Where to return the interface. NULL is returned for any HRESULT other than S_OK |

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The function was successful. |
| S_FALSE | There is nothing to enumerate (There are no items in the group). |
| E_OUTOFMEMORY | Not enough memory |
| E_INVALIDARG | An argument to the function was invalid (e.g. a bad riid parameter was passed.) |
| E_FAIL | The function was unsuccessful. |

Comments

The client must release the returned interface pointer when it is done with it.

### IOPCGroupStateMgt

IOPCGroupStateMgt allows the client to manage the overall state of the group. Primarily this allows changes to the update rate and active state of the group.

#### IOPCGroupStateMgt::GetState

HRESULT GetState(

[out] DWORD * pUpdateRate,

[out] BOOL * pActive,

[out, string] LPWSTR * ppName,

[out] LONG * pTimeBias,

[out] FLOAT * pPercentDeadband,

[out] DWORD * pLCID,

[out] OPCHANDLE * phClientGroup,

[out] OPCHANDLE * phServerGroup

);

Description

Get the current state of the group.

| Parameters | Description |
| --- | --- |
| pUpdateRate | The current update rate. The Update Rate is in milliseconds |
| pActive | The current active state of the group. |
| ppName | The current name of the group |
| pTimeBias | The TimeZone Bias of the group (in minutes) |
| pPercentDeadband | The percent change in an item value that will cause an exception report of that value to a client. This parameter only applies to items in the group that have dwEUType of Analog. [See discussion of Percent Deadband in Section 4.4.1] |
| pLCID | The current LCID for the group. |
| phClientGroup | The client supplied group handle |
| phServerGroup | The server generated group handle |

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| E_FAIL | The operation failed. |
| E_OUTOFMEMORY | Not enough memory |
| E_INVALIDARG | An argument to the function was invalid. |
| S_OK | The operation succeeded. |

Comments

This function is typically called to obtain the current values of this information prior to calling SetState. This information was all supplied by or returned to the client when the group was created. This function is also useful for debugging.

All out arguments must be valid pointers.  The marshaling mechanism requires valid pointers for proper behavior. NULL pointers will throw an RPC exception.

The client must free the returned ppName string.

#### IOPCGroupStateMgt::SetState

HRESULT SetState(

[unique, in] DWORD * pRequestedUpdateRate,

[out] DWORD * pRevisedUpdateRate,

[unique, in] BOOL *pActive,

[unique, in] LONG * pTimeBias,

[unique, in] FLOAT * pPercentDeadband

[unique, in] DWORD * pLCID,

[unique, in] OPCHANDLE *phClientGroup

);

Description

Client can set various properties of the group. Pointers to ‘in’ items are used so that the client can omit properties he does not want to change by passing a null pointer.

The pRevisedUpdateRate argument must contain a valid pointer.

| Parameters | Description |
| --- | --- |
| pRequestedUpdateRate | New update rate requested for the group by the client |
| pRevisedUpdateRate | Closest update rate the server is able to provide for this group. |
| pActive | TRUE (non-zero) to active the group. FALSE (0) to deactivate the group. |
| pTimeBias | TimeZone Bias if Group (in minutes) |
| pPercentDeadband | The percent change in an item value that will cause an exception report of that value to a client. This parameter only applies to items in the group that have dwEUType of Analog. [See discussion of Percent Deadband in Section 4.4.1] |
| pLCID | The Localization ID to be used by the group. |
| phClientGroup | New client supplied handle for the group. This handle is returned in the data stream provided to the client’s IAdvise by the Groups IDataObject. |

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| E_FAIL | The operation failed. |
| E_OUTOFMEMORY | Not enough memory |
| E_INVALIDARG | An argument to the function was invalid. |
| S_OK | The operation succeeded. |
| OPC_S_UNSUPPORTEDRATE | The server does not support the requested data rate but will use the closest available rate. |

Comments

For public groups, the server maintains unique state information for each client for Active, pUpdateRate, TimeZone. That is, the public groups behave as if each client had it’s own private copy.

Refer to Data Acquistion Section for details on the behavior of an OPC server with respect to the Synchronous and Asynchronous interfaces and Active state of groups.

#### IOPCGroupStateMgt::SetName

HRESULT SetName(

[in, string] LPCWSTR szName,

);

Description

Change the name of a private group. The name must be unique. The name cannot be changed for public groups.

| Parameters | Description |
| --- | --- |
| szName | New name for group. |

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| E_FAIL | The operation failed. |
| E_OUTOFMEMORY | Not enough memory |
| E_INVALIDARG | An argument to the function was invalid. |
| S_OK | The operation succeeded. |
| OPC_E_DUPLICATENAME | Duplicate name not allowed. |

Comments

Group names are required to be unique with respect to an individual client to server connection.

#### IOPCGroupStateMgt::CloneGroup

HRESULT CloneGroup(

[in, string] LPCWSTR szName,

[in] REFIID riid,

[out, iid_is(riid)] LPUNKNOWN * ppUnk

);

Description

Creates a second copy of a group with a unique name . This works for both public and private groups. However, the new group is always a private group. Most of the group and item properties are duplicated. The exceptions are

Active Status of group is set to FALSE

A new ServerHandle for the group is produced.

| Parameters | Description |
| --- | --- |
| szName | Name of the group. The name must be unique among the other groups created by this client. If no name is provided (szName is NULL) the server will generate a unique name. The server generated name will also be unique relative to any existing public groups. |
| riid | requested interface type |
| ppUnk | place to return interface pointer. NULL is returned for any HRESULT other than S_OK |

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded. |
| E_FAIL | The operation failed. |
| E_OUTOFMEMORY | Not enough memory |
| E_INVALIDARG | An argument to the function was invalid. |
| OPC_E_DUPLICATENAME | Duplicate name not allowed. |
| E_NOINTERFACE | The interface(riid) asked for is not supported by the server. |

Comments

This represents a new group which is independent of the original group. As with AddGroup the initial reference count of this new group is at least 2. As with AddGroup the group must be deleted with RemoveGroup when the client is done with it.

The client must also release the returned interface when it is no longer needed.

### IOPCPublicGroupStateMgt

This optional interface is used to convert a private group to a public group. Servers optionally provide this interface on group objects. A group created by a client is always created initially as a private group. This interface can be obtained from that private group in order to convert the group to a public group.

#### IOPCPublicGroupStateMgt::GetState

HRESULT GetState(

[out] BOOL * pPublic

);

Description

Used to determine if a particular group is public or not. If the interface is missing then all groups in the server are private.

| Parameters | Description |
| --- | --- |
| pPublic | TRUE if the group is public, FALSE if it is private |

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| E_FAIL | The operation failed. |
| E_INVALIDARG | An argument to the function was invalid. |
| S_OK | The operation succeeded. |

Comments

A server which supports public groups can provide this interface for any group (private or public). In practice a client will generally know for each group whether it is private or public. However, this method is useful for debugging.

#### IOPCPublicGroupStateMgt::MoveToPublic

HRESULT MoveToPublic(

void

);

Description

Converts a private group to a public group. The group must have a name which must be unique among all existing public groups. The state of the group (active, UpdateRate, IAdvise connections, etc.) for the calling client is not affected.

| Parameters | Description |
| --- | --- |
| void |  |

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The function was successful. |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |
| OPC_E_DUPLICATENAME | Duplicate Name not allowed |

Comments

A public group cannot be converted back to a private group. However it can be ‘cloned’ into a new private group.

For public groups, the update rate, client group handle and active status are maintained as ‘instance’ data for each client.

The client is required to set the client groupHandle before any asynchronous functions are performed on a  public group.  After the group is made public other clients can connect to the group. Generally, they must set their client instance information (e.g. group and item handles) prior to using the other standard group interfaces associated with a group.

Once a group is made public, items cannot be added or deleted.

For the items in the group, the client handle, active status and requested data type are maintained as ‘instance’ data for each client.

### IOPCSyncIO

IOPCSyncIO allows a client to perform synchronous read and write operations to a server. The operations will run to completion.

Refer to the Data Acquisition and Active State Behavior table for an overview of  the server data acquisition behavior and it’s affect on functionality within this interface.

Also refer to the Serialization and Syncronization issues section earlier in this document.

#### IOPCSyncIO::Read

HRESULT Read(

[in] OPCDATASOURCE dwSource,

[in] DWORD dwNumItems,

[in, size_is(dwNumItems)] OPCHANDLE * phServer,

[out, size_is(,dwNumItems)] OPCITEMSTATE ** ppItemValues,

[out, size_is(,dwNumItems)] HRESULT ** ppErrors

);

Description

This function reads the value, quality and timestamp information for one or more items in a group.  The function runs to completion before returning.  The data can be read from CACHE in which case it should be accurate to within the ‘UpdateRate’ and percent deadband of the group. The data can be read from the DEVICE in which case an actual read of the physical device is to be performed. The exact implementation of CACHE and DEVICE reads is not defined by this specification.

When reading from CACHE, the data is only valid if both the group and the item are active. If either the group or the item is inactive, then  the Quality will indicate out of service (OPC_QUALITY_OUT_OF_SERVICE).  Refer to the discussion of the quality bits later in this document for further information.

DEVICE  reads are not affected by the ACTIVE state of the group or item.

Refer to the Data Acquisition and Active State Behavior table earlier in this document for an overview of  the server data acquisition behavior and it’s affect on functionality within this interface.

| Parameters | Description |
| --- | --- |
| dwSource | The ‘data source’; OPC_DS_CACHE or OPC_DS_DEVICE |
| dwNumItems | The number of items to be read. |
| phServer | The list of server item handles for the items to be read |
| ppItemValues | Array of structures in which the item values are returned. |
| ppErrors | Array of HRESULTs indicating the success of the individual item reads. The errors correspond to the handles passed in phServer. This indicates whether the read succeeded in obtaining a defined value, quality and timestamp. NOTE any FAILED error code indicates that the corresponding Value, Quality and Time stamp are UNDEFINED. |

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded. |
| S_FALSE | The operation succeeded but there are one or more errors in ppErrors. Refer to individual error returns for more infomation. |
| E_FAIL | The operation failed. |
| E_OUTOFMEMORY | Not enough memory |
| E_INVALIDARG | An argument to the function was invalid. |

ppError Codes

| Return Code | Description |
| --- | --- |
| S_OK | Successful Read. |
| E_FAIL | The Read failed for this item |
| OPC_E_BADRIGHTS | The item is not readable |
| OPC_E_INVALIDHANDLE | The passed item handle was invalid. |
| OPC_E_UNKNOWNITEMID | The item is no longer available in the server address space. |
| OPC_E_* OPC_S_* | Vendor specific errors may also be returned. Descriptive information for such errors can be obtained from GetErrorString. |

Comments

If the HRESULT is S_OK, then ppError can be ignored (all results in it are guaranteed to be S_OK).

If the HRESULT is S_FALSE, then ppError will indicate which the status of each individual Item Read.

If the HRESULT is any FAILED code then (as noted earlier) the server should return NULL pointers for all OUT parameters including ppErrors.

For any FAILED ppError code the client should assume the curresponding ITEMSTATE is undefined. The Server should set the corresponding ITEMSTATE VARIANT to VT_EMPTY.

Note that here (as in the OPCItemMgt methods)  OPC_E_INVALIDHANDLE on one item will not affect the processing of other items and will cause the main HRESULT to return as S_FALSE

Expected behavior is that a CACHE read should be completed very quickly (within milliseconds). A DEVICE read may take a very long time (many seconds or more). Depending on the details of the implementation (e.g. which threading model is used) the DEVICE read may also prevent any other operations from being performed on the server by any other clients.

For this reason Clients are expected to use CACHE reads in most cases. DEVICE reads are intended for ‘special’ circumstances such as diagnostics.

The ppValues and ppErrors array are allocated by the server and must be freed by the client. Be sure to call VariantClear() on the variant in the ITEMRESULT.

#### IOPCSyncIO::Write

HRESULT Write(

[in] DWORD dwNumItems,

[in, size_is(dwNumItems)] OPCHANDLE * phServer,

[in, size_is(dwNumItems)] VARIANT * pItemValues,

[out, size_is(,dwNumItems)] HRESULT ** ppErrors

);

Description

Writes values to one or more items in a group. The function runs to completion. The values are written to the DEVICE. That is, the function should not return until it verifies that the device has actually accepted (or rejected) the data.

Writes are not affected by the ACTIVE state of the group or item.

| Parameters | Description |
| --- | --- |
| dwNumItems | Number of items to be written |
| phServer | The list of server item handles for the items to be read |
| pItemValues | List of values to be written to the items. The datatypes of the values do not need to match the datatypes of the target items. However an error will be returned if a conversion cannot be done. |
| ppErrors | Array of HRESULTs indicating the success of the individual item Writes. The errors correspond to the handles passed in phServer. This indicates whether the target device or system accepted the value. NOTE any FAILED error code indicates that the value was rejected by the device. |

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded. |
| S_FALSE | The operation succeeded but there are one or more errors in ppErrors. Refer to individual error returns for more infomation. |
| E_FAIL | The operation failed. |
| E_OUTOFMEMORY | Not enough memory |
| E_INVALIDARG | An argument to the function was invalid. |

ppError Codes

| Return Code | Description |
| --- | --- |
| S_OK | The function was successful. |
| E_FAIL | The function was unsuccessful. |
| OPC_S_CLAMP | The value was accepted but was clamped. |
| OPC_E_RANGE | The value was out of range. |
| OPC_E_BADTYPE | The passed data type cannot be accepted for this item (See comment) |
| OPC_E_BADRIGHTS | The item is not writeable |
| OPC_E_INVALIDHANDLE | The passed item handle was invalid. |
| OPC_E_UNKNOWNITEMID | The item is no longer available in the server address space |
| OPC_E_* OPC_S_* | Vendor specific errors may also be returned. Descriptive information for such errors can be obtained from GetErrorString. |

Comments

If the HRESULT is S_OK, then ppError can be ignored (all results in it are guaranteed to be S_OK).

If the HRESULT is any FAILED code then (as noted earlier) the server should return NULL pointers for all OUT parameters.

Note that here (as in the OPCItemMgt methods)  OPC_E_INVALIDHANDLE on one item will not affect the processing of other items and will cause the main HRESULT to return as S_FALSE

As an alternative to OPC_E_BADTPYE it is acceptable for the server to return any FAILED error returned by VariantChangeType or VariantChangeTypeEx.

A DEVICE write may take a very long time (many seconds or more). Depending on the details of the implementation (e.g. which threading model is used) the DEVICE write may also prevent any other operations from being performed on the server by any other clients.

For this reason Clients are expected to use ASYNC write rather than SYNC write in most cases.

The ppErrors array is allocated by the server and must be freed by the client.

### IOPCAsyncIO

IOPCAsyncIO  allows a client to perform asynchronous read and write operations to a server. The operations will be ‘queued’ and the function will return immediately so that the client can continue to run. Each operation is treated as a ‘transaction’ and is associated with a transaction ID. As the operations are completed, a callback will be made to the IAdvise Sink in the client (if one has been established). The information in the callback will indicate the transaction ID and the error results.  By convention, 0 is an invalid transaction id.

Also the expected behavior is that for any one transaction to Async Read, Write and Refresh, ALL of the results of that transaction will be returned in a single call to OnDataChange.

A server must be able to ‘queue’ at least one transaction of each type (read, write, refresh) for each group. It is acceptable for a server to return an error (CONNECT_E_ADVISELIMIT) if more than one transaction of the same type is performed on the same group by the same client. Server vendors may of course support queueing of additional transactions if they wish.

All operations are expected to complete even if they complete with an error. The concept of ‘time-out’ is not explicitly addressed in this specification however it is expected that where appropriate the server will internally implement any needed time-out logic.

Client Implementation Note:

The Transaction ID is generated by the Server and returned to the client in the callback. Some clients may want to save the ID returned by the server in some list of ‘outstanding transactions’ in order to verify completion of a transaction. This could be complicated if the OnDataChange callback occurs before the client has saved the returned ID.

Note: Version 1.0 of this specification suggested an approach involving critical sections. However, depending on the mix of client and server threading models used, it has been found in practice that the OnDataChange callback can occur within the same thread as the Read or Write and in fact can occur before the Read or Write returns to the caller.  Clearly, critical sections cannot resolve this case.

Although it has also been found in practice that many clients do not actually need to record the transaction ID (the Group’s ClientHandle is generally sufficient to identify the returned data), the following possible approach is suggested for those cases where this is needed.

Mainline Code

START CRITICAL SECTION

RECORD ALL NEEDED INFO ABOUT TRANSACTION EXCEPT TID.

CLEAR ‘TID COMPLETED’

SET A SPECIAL FLAG: ‘TID PENDING’

IOPCAsyncIO::Read or Write or Refresh

CHECK ‘TID COMPLETED’

IF SET AND EQUAL TO RETURNED TID THEN TRANSACTION IS COMPLETE

ELSE SAVE TRANSACTION ID IN LIST OF PENDING TRANSACTIONS

CLEAR ‘TID PENDING’

END CRITICAL SECTION

…

OnDataChange Code

START CRITICAL SECTION

READ DATA STREAM AND LOCATE TRANSACTION ID

LOCATE TRANSACTION ID IN LIST OF PENDING TRANSACTIONS

IF NOT FOUND, CHECK ‘TID PENDING’

IF ‘TID PENDING’ SET THEN RECORD THIS TID IN ‘TID COMPLETED’

END CRITICAL SECTION

…

#### IOPCAsyncIO::Read

HRESULT Read(

[in] DWORD dwConnection,

[in] OPCDATASOURCE dwSource,

[in] DWORD dwNumItems,

[in, size_is(dwNumItems)] OPCHANDLE * phServer,

[out] DWORD *pTransactionID,

[out, size_is(,dwNumItems)] HRESULT ** ppErrors

);

Description

Read one or more items in a group. The results are returned via the IAdvise Sink connection established through the IDataObject.

For CACHE reads the data is only valid if both the group and the item are active.

DEVICE reads are not affected by the ACTIVE state of the group or item.

| Parameters | Description |
| --- | --- |
| dwConnection | The OLE Connection number returned from IDataObject::DAdvise. This is passed to help the server determine which advise sink to call when the request completes. |
| dwSource | The data source; OPC_DS_CACHE or OPC_DS_DEVICE |
| dwNumItems | Number of items to be read. |
| phServer | Array of server item handles of the items to be read |
| pTransactionID | Place to return a Server generated transaction ID. This is included in the ‘completion’ information provided to the IAdvise. |
| ppErrors | Array of errors for each item - returned by the server. Indicates only if the corresponding server handle was valid. Any other errors (communications time-out, access rights, etc.) will be returned in the callback. Note that at this time the only item level status information available in the callback is the QUALITY field. |

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded. The read was successfully initiated |
| E_FAIL | The operation failed. |
| E_OUTOFMEMORY | Not enough memory |
| E_INVALIDARG | An argument to the function was invalid. |
| S_FALSE | One or more of the passed handles was invalid. The ppError array indicates which handles in phServer were invalid. NOTE if any handle is invalid this error is returned and the entire ASYNC Read operation is rejected. No callback will occur. |
| CONNECT_E_NOCONNECTION | The client has not registered a callback of type OPCSTMFORMATDATA or OPCSTMFORMATDATATIME through IDataObject:DAdvise. |

ppError Codes

| Return Code | Description |
| --- | --- |
| S_OK | The corresponding Item handle was valid. |
| OPC_E_INVALIDHANDLE | The corresponding Item handle was invalid |

Comments

If the HRESULT is S_OK, then ppError can be ignored (all results in it are guaranteed to be S_OK).

If the HRESULT is any FAILED code then (as noted earlier) the server should return NULL pointers for all OUT parameters. Note that in this case no Callback will occur.

Note that there is a difference in the handling of OPE_E_INVALIDHANDLE between SYNC read and ASYNC read. In this case (ASYNC read) an INVALIDHANDLE on one item will cause the entire request to be rejected and will cause the main HRESULT to return as S_FALSE. In this case the ppErrors will contain one or more OPC_E_INVALIDHANDLE errors and no callback will occur.

The only item specific error checking done by this call is to validate the passed handles. Thus ppErrors always contains values of either S_OK or OPC_E_INVALIDHANDLE. If all of the passed handles are valid and the operation is performed then all item level error returns will be via OnDataChange. Note that at this time the only item level status information available in the Callback is the QUALITY field.

NOTE: all of the results must be returned by the server in a single callback.

If the items in the group require multiple physical transactions to one or more physical devices then the server must wait until all of them are complete before invoking OnDataChange.

The Client must free the returned ppError array.

The transaction ID generated by the server should be globally unique and non-zero.

The transaction ID is used to identify the results that are returned in the OnDataChange.  The client may also use the transactionID when attempting to cancel an in progress asynchronous function

#### IOPCAsyncIO::Write

HRESULT Write(

[in] DWORD dwConnection,

[in] DWORD dwNumItems,

[in, size_is(dwNumItems)] OPCHANDLE * phServer,

[in, size_is(dwNumItems)] VARIANT * pItemValues,

[out] DWORD *pTransactionID,

[out, size_is(,dwNumItems)] HRESULT ** ppErrors

);

Description

Write one or more items in a group. The results are returned via the IAdviseSink connection established through the IDataObject.

| Parameters | Description |
| --- | --- |
| dwConnection | The OLE Connection number returned from IDataObject::DAdvise. This is passed to help the server determine which advise sink to call when the request completes. |
| dwNumItems | Number of items to be written |
| phServer | List of server items handles for the items to be written |
| pItemValues | List of values to be written. The value data types do not match the requested or canonical item datatype but must be ‘convertible’ to the canonical type. |
| pTransactionID | Place to return a Server generated transaction ID. This is included in the ‘completion’ information provided to the IAdvise. |
| ppErrors | Array of errors for each item - returned by the server. Indicates only if the corresponding server handle was valid. Any other errors (communications time-out, access rights, etc.) will be returned in the callback. |

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded. |
| E_FAIL | The operation failed. |
| E_OUTOFMEMORY | Not enough memory |
| E_INVALIDARG | An argument to the function was invalid. |
| S_FALSE | One or more of the passed handles was invalid. The ppError array indicates which handles in phServer were invalid. NOTE that if any handle is invalid this error is returned and the entire operation is rejected. No callback will occur. |
| CONNECT_E_NOCONNECTION | The client has not registered a callback of type OPCSTMFORMATWRITECOMPLETE through IDataObject:DAdvise. |

ppError Codes

| Return Code | Description |
| --- | --- |
| S_OK | The corresponding Item handle was valid. |
| OPC_E_INVALIDHANDLE | The corresponding Item handle was invalid |

Comments

If the HRESULT is S_OK, then ppError can be ignored (all results in it are guaranteed to be S_OK).

If the HRESULT is any FAILED code then (as noted earlier) the server should return NULL pointers for all OUT parameters. Note that in this case no Callback will occur.

Note that there is a difference in the handling of OPE_E_INVALIDHANDLE between SYNC write and ASYNC write. In this case (ASYNC write) an INVALIDHANDLE on one item will cause the entire request to be rejected and will cause the main HRESULT to return as S_FALSE. In this case the ppErrors will contain one or more OPC_E_INVALIDHANDLE errors and no callback will occur.

The only item specific error checking done by this call is to validate the passed handles. . Thus ppErrors always contains values of either S_OK or OPC_E_INVALIDHANDLE. If all of the passed handles are valid and the operation is performed then all item level error returns will be via OnDataChange.  These error codes have the same values as those returned by IOPCSyncIO::Write.

NOTE: all of the results must be returned by the server in a single callback.

If the items in the group require multiple physical transactions to one or more physical devices then the server must wait until all of them are complete before invoking OnDataChange.

Client must free the returned ppError array.

See the notes under ‘Read’ regarding the transaction ID.

#### IOPCAsyncIO::Refresh

HRESULT Refresh(

[in] DWORD dwConnection,

[in] OPCDATASOURCE dwSource,

[out] DWORD *pTransactionID

);

Description

Force a callback for all active items in the group (whether they have changed or not).  Inactive items are not included in the callback.

| Parameters | Description |
| --- | --- |
| dwConnection | The OLE Connection number returned from IDataObject::DAdvise. This is passed to help the server determine which advise sync to call when the request completes. |
| dwSource | Data source CACHE or DEVICE |
| pTransactionID | Place to return a Server generated transaction ID. This is included in the ‘completion’ information provided to the IAdvise. |

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded. |
| E_FAIL | The operation failed. (See notes below) |
| E_OUTOFMEMORY | Not enough memory |
| E_INVALIDARG | An argument to the function was invalid. |
| CONNECT_E_NOCONNECTION | The client has not registered a callback of type OPCSTMFORMATDATA or OPCSTMFORMATDATATIME through IDataObject:DAdvise. |

Comments

If the HRESULT is any FAILED code then no Callback will occur.

Calling  refresh for an InActive Group will return E_FAIL. Calling refresh for an Active Group, where all the items in the group are InActive also returns E_FAIL.

The behavior of this function is identical to what happens when DAdvise is called using ADVF_PRIMEFIRST except that the Callback will include a non-zero transaction ID.

Functionally it is also similar to what could be achieved by doing a READ from CACHE of all of the active items in a group.

NOTE: all of the results must be returned in a single callback.

If the items in the group require multiple physical transactions to one or more physical devices then the server must wait until all of them are complete before invoking OnDataChange.

The expected behavior is that this Refresh will not affect the timing of normal OnDataChange callbacks which are based on the UpdateRate.  For example, if the update rate is 1 hour and this method is called after 45 minutes then the server should still do its internal ‘checking’ at the end of the hour (15 minutes after the Refresh call).  Calling this method may affect the contents of that next callback (15 minutes later) since only items where the value or status changed during that 15 minutes would be included.  Items which had changed during the 45 minutes preceding the Refresh will be sent (along with all other values) as part of the Refresh Transaction. They would not be sent a second time at the end of the hour.  The value sent in response to the Refresh becomes the ‘last value sent’ to the client when performing the normal subscription logic.

See the notes under ‘Read’ regarding the transaction ID.

#### IOPCAsyncIO::Cancel

HRESULT Cancel(

[in] DWORD dwTransactionID

);

Description

Request that the server cancel an outstanding transaction.

| Parameters | Description |
| --- | --- |
| dwTransactionID | The transaction ID which was associated with the operation to be canceled. |

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded. |
| E_FAIL | The operation failed. Either the transaction ID was invalid or it was ‘too late’ to cancel the transaction. |

Comments

The exact behavior (for example whether an operation that has actually started will be aborted) will be server specific and will also depend on the timing of the cancel request.  Also, depending on the timing, a Callback for the transaction may or may not occur.  This method is intended to be used during shutdown of a task.

In general, if this operation succeeds then no callback will occur. If this operation fails then a callback may occur (or may already have occured).

### IEnumOPCItemAttributes

IEnumOPCItemAttributes allows a client to find out the contents (items) of a group and the attributes of those items.

NOTE: most of the returned information was either supplied by or returned to the client at the time it called AddItem.

The optional EU information (see the OPCITEMATTRIBUTES discussion) may be very useful to some clients.  This interface is also useful for debugging or for enumerating the contents of a public group.

This interface is returned only by IOPCItemMgt::CreateEnumerator.  It is not available through query interface.

Since enumeration is a standard interface this is described only briefly.

See the OLE Programmer’s reference for error codes.

#### IEnumOPCItemAttributes::Next

HRESULT Next(

[in] ULONG celt,

[out, size_is(,*pceltFetched)] OPCITEMATTRIBUTES ** ppItemArray,

[out] ULONG * pceltFetched

);

Description

Fetch the next ‘celt’ items from the group.

| Parameters | Description |
| --- | --- |
| celt | number of items to be fetched. |
| ppItemArray | Array of OPCITEMATTRIBUTES. Returned by the server. |
| pceltFetched | Number of items actually returned. |

Comments

The client must free the returned OPCITEMATTRIBUTES structure including the contained items; szItemID, szAccessPath, pBlob, vEUInfo.

#### IEnumOPCItemAttributes::Skip

HRESULT Skip(

[in] ULONG celt

);

Description

Skip over the next ‘celt’ attributes.

| Parameters | Description |
| --- | --- |
| celt | Number of items to skip |

Comments

Skip is probably not useful in the context of OPC.

#### IEnumOPCItemAttributes::Reset

HRESULT Reset(

void

);

Description

Reset the enumerator back to the first item.

| Parameters | Description |
| --- | --- |
| void |  |

Comments

#### IEnumOPCItemAttributes::Clone

HRESULT Clone(

[out] IEnumOPCItemAttributes** ppEnumItemAttributes

);

Description

Create a 2nd copy of the enumerator. The new enumerator will initially be in the same ‘state’ as the current enumerator.

| Parameters | Description |
| --- | --- |
| ppEnumItemAttributes | Place to return the new interface |

Comments

The client must release the returned interface pointer when it is done with it.

### IDataObject

The OPC Specification requires the IDataObject to be implemented for the OPC servers.

IDataObject is implemented on the OPCGroup rather than on the individual items. This allows the creation of an Advise connection between the client and the group using the OPC Data Stream Formats for the efficient data transfer.

It is required that the following methods be supported.

DAdvise

DUnadvise

Because the IDataObject deals with a STREAM rather than individual items, the following methods do not need to be supported (they can be implemented as stubs which return E_NOTIMPL.

GetData

GetDataHere

GetCanonicalFormatEtc

The server vendor may chose to implement additional methods on the IDataObject.  It is the intent of this design that data items be transferred to applications primarily via the Advise connection or via the Synchronous or Asynchronous Read methods.

The data returned to the Advise connection is returned via a IAdviseSink which receives data in a Global Memory Section also referred to here as the ‘stream’. These streams can be in several formats.  They are used to provide exception data as well as completion information for Async Reads and Writes. The stream formats are

“OPCSTMFORMATDATA”

“OPCSTMFORMATDATATIME”

“OPCSTMFORMATWRITECOMPLETE”

Use the function

RegisterClipboardFormat()

to obtain the format value (cfFormat) to be used for data transfers between OPC client applications and OPC server applications.

The registered callback function (OnDataChange in the client’s IAdviseSink) may be specified by the client application so that it spans multiple groups.  Information about the group (the Group’s ClientHandle) must be provided to the client application as part of the stream so that the client can successfully interpret the items that are contained in the data stream.  Each data stream will only contain the items defined within the specified group.

Because of the nature of the asynchronous calls, OLE requires that no synchronous calls are made from a method that has been called asynchronously (as all of the IAdviseSink methods are) which would cause the asynchronous function to be blocked.  It is very important that the methods that are called asynchronously (the IAdviseSink methods)  have limited processing, and return quickly.  Lengthy processing should be done outside of the context of the asynchronous method that has been invoked.

It is the client application’s responsibility to keep up with the data changes that the server (configured by the client app) sends.  The client should assume that the server may send data at the update rate specified in the group, and that for each group that identical throughput may occur. Various Windows and OLE related internal errors can result if the server sends data faster than the client can receive it. The performance of the OPC servers and OPC clients is highly tied to the developers implementation of these critical interfaces.

The server should be implemented to optimize the acquisition of the data items for multiple clients wherever possible.  This means that it is best for the server to read data from devices at the fastest rate possible: (a) to support the needs of multiple clients configured for the same item or (b), if a single client has configured the same item in different groups at different update rates.

Refer to the OLE programming manual for a tutorial and guide to implementing the required functionality.

#### IDataObject::DAdvise

HRESULT DAdvise(

FORMATETC *pFmt,

DWORD adv,

LPADVISESINK pSnk,

DWORD * pConnection

);

Description

Create a connection for a particular ‘stream’ format between the OPC Group and the Client.

| Parameters | Description |
| --- | --- |
| pFmt | The format in which the client is interested. This will always be one of the three supported OPC formats as described below. |
| adv | Data Advise Flags specifier. Not used by OPC. |
| pSnk | Pointer to the Client’s IAdviseSink |
| pConnection | OLE Connection key for use with IOPCAsyncIO and UnAdvise |

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The function was successful. |
| CONNECT_E_ADVISELIMIT | The group cannot support additional connections of this type. |
| For other codes see the OLE programmers reference |  |

Comments

Since groups are specific to a client, it is sufficient for OPC Compliance that a group support only a single ‘connection point’ for each stream format. A second attempt by the same client to subscribe to the same stream format on the same group may return CONNECT_E_ADVISELIMIT.

The Advise Flags Parameter (adv) is not used by OPC. Servers should ignore this parameter and should always send a copy of all data items when a connection is made. Note that this is equivalent to the behavior associated with ADVF_PRIMEFIRST.

It is expected that a client will assign unique values to the group and item client handles if they intend to use any of the asynchronous functions of the OPC interfaces, including IOPCAsyncIO, and IDataObject/IAdviseSink interfaces, since this is the only key to the information that the server provides back to the client with the OnDataChange stream.

The ‘formats’ really represent different types of events rather than different formats for the same data.

The FORMATETC must be filled in as follows;

fe.cfFormat = OPCSTMFORMATDATA or

OPCSTMFORMATDATATIME or

OPCSTMFORMATWRITECOMPLETE.

(See RegisterClipboardFormat())

fe.dwAspect = DVASPECT_CONTENT;

fe.ptd = NULL;

fe.tymed = TYMED_HGLOBAL;

fe.lindex = -1;

The storage medium will always be TYMED_HGLOBAL (for computability with DCOM).

#### IDataObject::DUnadvise

HRESULT DUnadvise(

DWORD Connection

);

Description

Terminate a connection between the OPC Group and the Client.

| Parameters | Description |
| --- | --- |
| Connection | The connection to be terminated |

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The function was successful. |
| For other codes see the OLE programmers reference |  |

Comments

## Client Side Interfaces

### IAdviseSink

The client need only provide a full implementation of OnDataChange. The other methods of IAdviseSink can be implemented as stubs since they will never be called.  Callbacks can occur for several reasons; simple Subscription, Async Read, Async Write, Refresh.  A client can be written such that it performs several of these operations in parallel.  In this case the client can determine the ‘cause’ of a particular callback by examining first the data format as provided in the FORMATETC and second the Transaction ID as contained in the stream.

Because of the nature of the asynchronous calls, OLE requires that no synchronous calls are made from a method that has been called asynchronously (as all of the IAdviseSink methods are) which would cause the asynchronous function to be blocked.  It is very important that the methods that are called asynchronously (the IAdviseSink methods)  have limited processing, and return quickly.  Lengthy processing should be done outside of the context of the asynchronous method that has been invoked.

It is client application responsibility to keep up with the data changes that the server has been configured by the client application to send.  The client should assume that the server may send data at the update rate specified in the group, and that for each group that identical throughput may occur. Various Windows and OLE related internal errors can result if the server sends data faster than the client can receive it. The performance of the OPC servers and OPC clients is highly tied to the developers implementation of these critical interfaces.

#### IAdviseSink::OnDataChange

HRESULT OnDataChange (

FORMATETC * pFE,

STGMEDIUM * pSTM

);

Description

This method is provided by the client to handle notifications from the OPC Group for exception based data changes, Async reads and Refreshes and Async Write Complete.

| Parameters | Description |
| --- | --- |
| pFE | the format of the data being receive by the sink |
| pSTM | the storage medium containing the data. |

Comments

This section will discuss the reasons why the client may receive callbacks, the contents of FORMATETC and the contents of the STGMEDIUM.

Note that in this case the caller (the server) owns and will free the storage.

The client should NOT free it.  Also note that the storage is valid only for the duration of the OnDataChange call.

Callbacks can occur for several reasons;

- One or more ‘data change’ events with timestamp (format will be OPCSTMFORMATDATATIME and transaction ID will be 0). This format is also used in response to a Refresh and ASYNC READ with a non-zero transaction ID.

- One or more ‘data change’ events without timestamp (format will be OPCSTMFORMATDATA and transaction ID will be 0). This format is also used in response to a Refresh and ASYNC READ with a non-zero transaction ID.

- Completion of an ASYNC WRITE. (format will be OPCSTMFORMATWRITECOMPLETE and transaction ID will be non-0)

The FORMATETC will be filled in as follows;

fe.cfFormat = OPCSTMFORMATDATA or

OPCSTMFORMATDATATIME or

OPCSTMFORMATWRITECOMPLETE.

fe.ptd = NULL;

fe.dwAspect = DVASPECT_CONTENT;

fe.lindex = -1;

fe.tymed = TYMED_HGLOBAL;

The storage medium will always be TYMED_HGLOBAL (for computability with DCOM). The global memory handle can be found in pSTM.hGlobal. GlobalLock() can be used to convert this to a pointer.

The data stored in the global memory by the server will have one of several structures depending on the Format (which depends on the event that generated the data).  Although the data resides in this structure in global memory, we refer to it as a ‘data stream’.

These three formats are summarized below and are described in detail later in the document.

OPCSTMFORMATDATATIME Data with TimeStamp

The data consists of a group header followed by one or more item headers followed by the data.

OPCGROUPHEADER

OPCITEMHEADER1[hdr.dwItemCount]

VARIANTS[hdr.dwItemCount]

OPCSTMFORMATDATA Data without TimeStamp

The data consists of a group header followed by one or more item headers followed by the data.

OPCGROUPHEADER

OPCITEMHEADER2[hdr.dwItemCount]

VARIANTS[hdr.dwItemCount]

OPCSTMFORMATWRITECOMPLETE Async Write Complete

The data consists of a group header followed by one or more item headers followed by the data.

OPCGROUPHEADERWRITE

OPCITEMHEADERWRITE[hdr.dwItemCount]

# OPC Automation Interface Design

## Overview

This versions of the specification reflects the current release of the automation interface.   A new revision of the interface is currently under construction.

The actual ODL specification of this interface is provided in Appendix A. Note that this interface is actually provided as a DUAL interface to allow for more efficient operation by client software that can take advantage of this. However the discussion which follows is of the IDispatch interface.

This chapter describes how we will expose the custom  interface through the IDispatch interface of OLE Automation. The IDispatch interfaces are fully supported by VC++ and Visual Basic (VB) 4.0.  They allow any application which has an OLE Automation Controller (e.g. VB, VC++, VBA in Excel and MS Project, Visio, etc.) to access the OPC Interface.

The automation interface for OPC is made up of an Object Hierarchy consisting of an OPC Server, Groups, and data Items as illustrated in Figure 5-1. Note that the groups are contained within the server object. The server object is a collection which allows for the use of the “FOR/NEXT” constructs in Visual Basic.

Note also that the objects exposed by the Automation Interface are in-process proxies of the ‘real’ objects in the OPCServer. This allows a high level of performance for the automation clients.

Figure 5-1.  Automation Object Hierarchy

| Object | Description |
| --- | --- |
| OPCServer | An instance of an OPC Data Server, e.g. SystemOPCServer. You must create an OPCServer object before you can get references to other objects. |
| OPCGroup | Holds on to scanning information, status information about the communication interface, and references to the OPCItems. |
| OPCItem | Holds on to the item’s definition, current value(s), status information, last update time, etc. |

Note that the OPCGroup and Item containers represent the lists of paths and items which the client application wants to access. Whether or not these items must previously be configured within the server or whether they are added ‘on the fly’ as needed is a function of the server implementation. For example a server for an existing DCS system might only be able to reference items that already exist within that DCS. However a server for a PLC might be smart enough to add and delete references to register variables from internal scanning tables ‘on-the-fly’ as needed by client applications.

Data Synchronization

Clients that explicitly poll for data via any of the various Read methods can be assured that the Value, Timestamp and Quality Properties of the items will be in sync with each other. Clients that register callbacks can similarly be assured that these properties will be in sync within the scope of the callback function. However if the two techniques are mixed in the same application it will be impossible for the client to ensure that the item properties are exactly in sync since a callback which changed the properties could occur between the time the client accesses the various properties.

Introduction to Exceptions

The Automation server allows callbacks on Async Refresh, Read and Write complete and On Data Change. The implementation assumes that the Automation Client is equipped to deal with these events.

An example follows showing how to create and use OPC Automation Objects as well as the Exception logic from VB.

Note that for a dual automation interface at the implementation level the properties are in fact Get/Set methods - for that reason these sections are organized to present the properties and methods in essentially the same organization - each method is appropriately labeled in the title.

## OPC Server Object

An object which has a connection to a running OPC Server, e.g. SystemOPCServer.  You must create an OPCServer object before you can create other objects such as groups and items.

The OPCServer supports several different Dispatch Interfaces.

Example

Dim MyServer as Object
Dim OPCServer as IOPCServerDisp
Set MyServer = CreateObject(“VendorX_OPCServer.1”)
Set OPCServer = MyServer

### IOPCServerDisp Interface

This is the default interface to the OPCServer Object. The interface is declared as a dual interface allowing automation clients to bind directly to the vtable.  The properties and methods of this interface are described in the following sections.

#### IOPCServerDisp::Count Property

ODL Syntax

[
	propget
]
	HRESULT Count([out, retval] long * pCount);

VB Syntax

Dim Svr as IOPCServerDisp
Dim Count as Long

Set Svr = CreateObject(“OPCVendorX_Server.1”)
Count = Svr.Count
MsgBox “There are “ & Count & “Groups defined”

Description

Return the number of Groups defined within the server’s address space.

Return Value

Long
The value of the Count property

parameters

None

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

#### IOPCServerDisp::_NewEnum Property

ODL Syntax

[
	propget, 
	restricted,
	id( DISPID_NEWENUM )
]
	HRESULT _NewEnum([out, retval] IUnknown ** ppUnk);

VB Syntax

Dim Svr as IOPCServerDisp
Dim Val as Variant

Set Svr = CreateObject(“OPCVendorX_Server.1”)
For Each Val in Svr
	MsgBox Val
Next Val

Description

Returns an enumerator that supports IEnumVariant for the items currently in the collection. Read-only property.

Return Value

Enumerator Object
The enumerator of the requested type.  See SetEnumeratorType.

parameters

None

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_FAIL | The function was unsuccessful. |

Comments

_NewEnum will not be accessible to users and must have the restricted attribute in the ODL file. The _NewEnum method must have a special DISPID, DISPID_NEWENUM. The defining characteristic of a collection is the ability for a user to iterate over the items in it. Some languages will have built-in support for collections. The _NewEnum property allows an OLE automation controller to support "for each" iteration over a collection.

#### IOPCServerDisp::StartTime Property

ODL Syntax

[

propget
]
	HRESULT StartTime([out, retval] DATE * pStartTime);

VB Syntax

Dim Svr as IOPCServerDisp
Dim Val as Date

Set Svr = CreateObject(“OPCVendorX_Server.1”)
Val = Svr.StartTime

Description

Get the time the server was started (in UTC).

Return Value

Date
The value of the StartTime property.

parameters

None

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_FAIL | The function was unsuccessful. |

Comments

The use of the date variant will allow Visual Basic to automatically convert the results of the function to whatever format is appropriate.

#### IOPCServerDisp::CurrentTime Property

ODL Syntax

[
	propget
]
	HRESULT CurrentTime([out, retval] DATE * pCurrentTime);

VB Syntax

Dim Svr as IOPCServerDisp
Dim Val as Date

Set Svr = CreateObject(“OPCVendorX_Server.1”)
Val = Svr.CurrentTime

Description

The current time (UTC) as known by the server.

Return Value

Date
The value of the CurrentTime property.

parameters

None

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

#### IOPCServerDisp::LastUpdateTime Property

ODL Syntax

[
	propget
]
	HRESULT LastUpdateTime([out, retval] DATE * pLastUpdateTime);

VB Syntax

Dim Svr as IOPCServerDisp
Dim Val as Date

Set Svr = CreateObject(“OPCVendorX_Server.1”)
Val = Svr.LastUpdateTime

Description

The time (UTC) the server sent the last data value update to this client. This value is maintained on an instance basis.

Return Value

Date
The value of the LastUpdateTime property.

parameters

None

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

#### IOPCServerDisp::MajorVersion Property

ODL Syntax

[
	propget
]
	HRESULT MajorVersion([out, retval] short *pMajorVersion);

VB Syntax

Dim Svr as IOPCServerDisp
Dim Val as Integer

Set Svr = CreateObject(“OPCVendorX_Server.1”)
Val = Svr.MajorVersion

Description

The major version of the server software.

Return Value

Short
The value of the MajorVersion property.

parameters

None

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

#### IOPCServerDisp::MinorVersion Property

ODL Syntax

[
	propget
]
	HRESULT MinorVersion([out, retval] short *pMinorVersion);

VB Syntax

Dim Svr as IOPCServerDisp
Dim Val as Integer

Set Svr = CreateObject(“OPCVendorX_Server.1”)
Val = Svr.MinorVersion

Description

The minor version of the server software.

Return Value

Short
The value of the MinorVersion property.

parameters

None

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

#### IOPCServerDisp::BuildNumber Property

ODL Syntax

[
	propget
]
	HRESULT BuildNumber([out, retval] short *pBuildNumber);

VB Syntax

Dim Svr as IOPCServerDisp
Dim Val as Integer

Set Svr = CreateObject(“OPCVendorX_Server.1”)
Val = Svr.BuildNumber

Description

The ‘build number’ of the server software.

Return Value

Short
The value of the BuildNumber property.

parameters

None

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

#### IOPCServerDisp::VendorInfo Property

ODL Syntax

[
	propget
]
	HRESULT VendorInfo([out, retval] BSTR * pVendorInfo);

VB Syntax

Dim Svr as IOPCServerDisp
Dim strVal as String

Set Svr = CreateObject(“OPCVendorX_Server.1”)
strVal = Svr.VenderInfo

Description

A vendor specific string providing additional information about the server. It is recommended that this mention the name of the company and the type of device(s) supported.

Return Value

Short
The value of the VendorInfo property.

parameters

None

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_FAIL | The function was unsuccessful. |

Comments

#### IOPCServerDisp::Item Method

ODL Syntax

HRESULT Item(	[in] VARIANT Item, 
			[out, retval] IDispatch ** ppDisp);

VB Syntax

Dim Svr as IOPCServerDisp
Dim Item as Object
Dim Item2 as Object

Set Svr = CreateObject(“OPCVendorX_Server.1”)
Set Item = Svr.Item(1)
Set Item2 = Svr.Item(“Group One”)

Description

Special method used by Automation to implement the FOR/NEXT feature of Basic.

Return Value

Object
The Object reference for the item in the collection.

parameters

Item
Index of the item to retrieve from the collection.

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_INVALIDARG | An Invalid Parameter was Passed. |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

The term Item in this context is a VB term which represents an item in a collection..  It has no relation to an OPCItem.

#### IOPCServerDisp::AddGroup Method

ODL Syntax

HRESULT AddGroup(	[in] BSTR Name,
	[in] boolean Active,
	[in] long ReqestedUpdateRate,
	[in] long ClientGroupHandle,
	[in] float *pPercentDeadband,
	[in] long LCID,
	[out] long *pServerGroupHandle,
	[out] long *pRevisedUpdateRate,
	[in, optional] VARIANT *pTimeBias,
	[out, retval] IDispatch **ppDisp);

VB Syntax

Dim Svr as IOPCServerDisp
Dim UpdateRate as long
Dim PercentDeadband as single
Dim ServerGroupHandle as long
Dim Group as Object


PercentDeadband = 1
Set Svr = CreateObject(“OPCVendorX_Server.1”)
Set Group = Svr.AddGroup(“Group One”, TRUE, 1000, 1, PercentDeadband, &H0409, ServerGroupHandle, UpdateRate)

Description

Add a new group to the server

Return Value

IDispatch *
The default IDispatch interface for the Group Object.

parameters

Name
Optional name of the group. The name must be unique among the other groups created by this client. If no name is provided, the server will generate a unique name.

Active
FALSE  if the Group is to be created inactive.  TRUE if the Group is to be created as active.

ReqestedUpdateRate
Determines the fastest rate at which data changes will be reported to the client. This is intended only to control the behavior of the interface. How the server deals with the update rate and how often it actually polls the hardware is an implementation detail.  Passing 0 indicates the server should use the fastest practical rate.

ClientGroupHandle
Client provided handle for this group.

pPercentDeadband
The percent change in an item value that will cause an exception report of that value to a client. This parameter only applies to items in the group that have dwEUType of Analog. [See discussion of Percent Deadband in Section 4.4.1].

LCID
The language to be used by the server when returning values (including EU enumeration’s) as text for operations on this group.  This could also include such things as alarm or status conditions or digital contact states.

pServerGroupHandle
Server provided handle for this group.

pRevisedUpdateRate
Place to store the rate at which the server will actually report data changes to the client. This may differ from the requested update rate.

pTimeBias
Containing the initial TimeBias for the Group.

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded. |
| E_INVALIDARG | An Invalid Parameter was Passed. |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

The Client should assign the returned value to an object of the desired type to access the interface needed.

For example:

#### IOPCServerDisp:: GetErrorString Method

ODL Syntax

HRESULT GetErrorString(	[in] long Error,
	[in] long Locale,
	[out, retval] BSTR * ErrorString);

VB Syntax

Dim Svr as IOPCServerDisp
Dim strErr as String 

Set Svr = CreateObject(“OPCVendorX_Server.1”)
strErr = Svr.GetErrorString(&H80010001, &H0409)

Description

Returns the error string for a server specific error code.

Return Value

BSTR
The string corresponding to the given error code and location id.

parameters

Error
A server specific error code that the client application had returned from an interface function from the server, and for which the client application is requesting the server’s textual representation.

Locale
The locale for the returned string.  E.g. The LCID for US English is 0x0409 (or &H409).

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_INVALIDARG | An Invalid Parameter was Passed. |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

#### IOPCServerDisp:: GetGroupByName Method

ODL Syntax

HRESULT GetGroupByName(	[in] BSTR Name,
	[out, retval] IDispatch ** ppDisp);

VB Syntax

Dim Svr as IOPCServerDisp
Dim Group as Object

Set Svr = CreateObject(“OPCVendorX_Server.1”)
Set Group = Svr.GetGroupByName(“Group One”)

Description

Given the name of a private group (created earlier by the same client), return an additional interface pointer.  Use GetPublicGroupByName to attach to public groups.

Return Value

IDispatch *
The default IDispatch interface for the Group Object.

parameters

Name
The name of the group. That is the group must have been created by the caller.

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_INVALIDARG | An Invalid Parameter was Passed. |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

#### IOPCServerDisp:: RemoveGroup Method

ODL Syntax

HRESULT RemoveGroup(	[in] long ServerGroupHandle,
	[in] boolean Force);

VB Syntax

Dim Svr as IOPCServerDisp
Dim Group as Object

Set Svr = CreateObject(“OPCVendorX_Server.1”)
Svr.RemoveGroup “Group Two”, TRUE

Description

Deletes the Group

Return Value

None

parameters

ServerGroupHandle
Handle for the group to be removed.

Force
Forces deletion of the group even if references are outstanding.

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_INVALIDARG | An Invalid Parameter was Passed. |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

Remove group will mark the group as ‘deleted’.  Any further calls to this group (via interfaces obtained earlier) will fail. When all the interfaces are released, the group will actually be deleted.  If Force is TRUE then the group is deleted unconditionally even if references still exist.

#### IOPCServerDisp:: SaveConfig Method

ODL Syntax

HRESULT SaveConfig([in] BSTR FileName);

VB Syntax

Dim Svr as IOPCServerDisp
Dim Group as Object
Dim UpdateRate as Integer

Set Svr = CreateObject(“OPCVendorX_Server.1”)
Svr.SaveConfig “ServerConfig.cfg”

Description

This method saves server configuration data for parameters such as serial port baud rate, etc. It is NOT intended for saving group and item configuration information.

Return Value

None

parameters

FileName
The name of the configuration file.

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_INVALIDARG | An Invalid Parameter was Passed. |
| E_OUTOFMEMORY | Not enough memory |
| E_NOTIMPL | The function is not implemented in the server. |
| E_FAIL | The function was unsuccessful. |

#### IOPCServerDisp:: LoadConfig Method

ODL Syntax

HRESULT LoadConfig([in] BSTR FileName);

VB Syntax

Dim Svr as IOPCServerDisp
Dim Group as Object
Dim UpdateRate as Integer

Set Svr = CreateObject(“OPCVendorX_Server.1”)
Svr.LoadConfig “ServerConfig.cfg”

Description

This method loads server configuration data for parameters such as serial port baud rate, etc. It is NOT intended for loading group and item configuration information.

Return Value

None

parameters

FileName
The name of the configuration file.

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_INVALIDARG | An Invalid Parameter was Passed. |
| E_OUTOFMEMORY | Not enough memory |
| E_NOTIMPL | The function is not implemented in the server. |
| E_FAIL | The function was unsuccessful. |

#### IOPCServerDisp::SetEnumeratorType

ODL Syntax

HRESULT SetEnumeratorType(	[in] long Scope,
[in] short Type);

VB Syntax

Dim Svr as IOPCServerDisp
Dim Group as Object
Dim GroupName as String

Set Svr = CreateObject(“OPCVendorX_Server.1”)

Svr.SetEnumeratorType OPC_ENUM_PRIVATE_CONNECTIONS, OPC_GROUP_ENUM
For Each Group in Svr

MsgBox Group.Name
Next Group

Svr.SetEnumeratorType OPC_ENUM_PUBLIC_CONNECTIONS, OPC_GROUPNAME_ENUM
For Each GroupName in Svr

MsgBox GroupName
Next GroupName

Description

Create various enumerators for the groups provided by the Server.

Return Value

None

parameters

Scope
Indicates the class of groups to be enumerated
OPC_ENUM_PRIVATE_CONNECTIONS enumerates the private groups the client is connected to (Default).
OPC_ENUM_PUBLIC_CONNECTIONS enumerates the public groups the client is connected to.
OPC_ENUM_ALL CONNECTIONS enumerates all of the groups the client is connected to.
OPC_ENUM_PRIVATE enumerates all of the private groups created by the client (whether connected or not)
OPC_ENUM_PUBLIC enumerates all of the public groups available in the server (whether connected or not)
OPC_ENUM_ALL enumerates all private groups and all public groups (whether connected or not)

Type
The interface requested. 
OPC_GROUPNAME_ENUM - an enumerator which iterates over group names (Default).
OPC_GROUP_ENUM  an enumerator which iterates over group objects

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_INVALIDARG | An Invalid Parameter was Passed. |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

Servers which do not support public groups will simply behave as if they had no public groups.  That is they will NOT return E_INVALIDARG if the mode includes public groups.

### IOPCServerPublicGroupsDisp

This optional interface to the OPCServer Object to allow management of public groups. Public Groups are discussed in detail in Section 4.3.4.

#### IOPCServerPublicGroupsDisp:: GetPublicGroupByName Method

ODL Syntax

HRESULT GetPublicGroupByName(	[in] BSTR Name,
	[out, retval] IDispatch **ppDisp);

VB Syntax

Dim Svr as IOPCServerDisp
Dim Group as Object

Set Svr = CreateObject(“OPCVendorX_Server.1”)
Set Group = Svr.GetPublicGroupByName(“Public Group One”)

Description

‘Connects’ the client to a public group. This returns an interface pointer to the group.

Return Value

IDispatch *
The default IDispatch interface for the public group object.

parameters

Name
Name of group to be connected.

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_INVALIDARG | An Invalid Parameter was Passed. |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

#### IOPCServerPublicGroupsDisp:: RemovePublicGroup Method

ODL Syntax

HRESULT RemovePublicGroup(	[in] long ServerGroupHandle,
	[in] boolean Force);

VB Syntax

Dim Svr as IOPCServerDisp
Dim Group as Object

Set Svr = CreateObject(“OPCVendorX_Server.1”)
Svr.RemovePublicGroup “Public Group Two”, FALSE

Description

Delete a public group.

Return Value

None

parameters

ServerGroupHandle
Handle for the group to be removed.

Force
Forces deletion of the group even if references are outstanding.

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_INVALIDARG | An Invalid Parameter was Passed. |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

Remove group will mark the group as ‘deleted’.  Any further calls to this group (via interfaces obtained earlier) will fail. When all the interfaces are released, the group will actually be deleted.  If Force is TRUE then the group is deleted unconditionally even if references still exist.

Any client can remove the public group.  You can get the server handle of the group by reading the IOPCGroupStateMgtDisp::ServerGroupHandle property.

### IOPCServerBrowseServerAddressSpaceDisp Interface

This optional interface to the OPCServer Object provides a way for clients to browse the available data items in the server. This provides the user with a list of the valid definitions for an ItemID.

#### IOPCServerBrowseServerAddressSpaceDisp::_NewEnum Property

ODL Syntax

[
	propget, 
	restricted,
	id( DISPID_NEWENUM )
]
	HRESULT _NewEnum([out, retval] IUnknown ** ppUnk);

VB Syntax

Dim Svr as IOPCServerBrowseServerAddressSpaceDisp
Dim Val as Variant

Set Svr = CreateObject(“OPCVendorX_Server.1”)
For Each Val in Svr
	MsgBox Val
Next Val

Description

Returns an enumerator that supports IEnumVariant for the strings currently in the collection. Read-only property.

Return Value

Enumerator Object
The enumerator of the requested strings.  See SetItemIDEnumerator and SetAccessPathEnumerator.

parameters

None

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_FAIL | The function was unsuccessful. |

Comments

_NewEnum will not be accessible to users and must have the restricted attribute in the ODL file. The _NewEnum method must have a special DISPID, DISPID_NEWENUM. The defining characteristic of a collection is the ability for a user to iterate over the items in it. Some languages will have built-in support for collections. The _NewEnum property allows an OLE automation controller to support "for each" iteration over a collection.

#### IOPCBrowseServerAddressSpaceDisp::Organization Property

ODL Syntax

[
	propget
]
	HRESULT Organization([out, retval] long *pNameSpaceType);

VB Syntax

Dim Svr as IOPCServerBrowseServerAddressSpaceDisp
Dim Org as long

Set Svr = CreateObject(“OPCVendorX_Server.1”)
Org = Svr.Organization

Description

Returns the type of name space (flat or hierarchical) for the server.

Return Value

Long
The value of the Organization property.

parameters

None

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_INVALIDARG | An Invalid Parameter was Passed. |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

#### IOPCBrowseServerAddressSpaceDisp:: ChangeBrowsePosition Method

ODL Syntax

HRESULT ChangeBrowsePosition(	[in] long BrowseDirection,
	[in] BSTR Position);

VB Syntax

Dim Svr as IOPCServerBrowseServerAddressSpaceDisp

Set Svr = CreateObject(“OPCVendorX_Server.1”)
Svr.ChangeBrowsePosition OPC_BROWSE_DOWN, “Level One”

Description

Provides a way to move “up” or “down” in a hierarchical space.

Return Value

None

parameters

BrowseDirection
OPC_BROWSE_UP or OPC_BROWSE_DOWN.

String
For DOWN, the name of the branch to move into. This would be one of the strings returned from BrowseOPCItemIDs.  For UP this parameter is ignored and should point to a NULL string.

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_INVALIDARG | An Invalid Parameter was Passed. |
| E_FAIL | The function was unsuccessful. |

Comments

The function will return E_FAIL if called for a FLAT space.

An error is returned if the passed string does not represent a ‘branch’ (has no children).

#### IOPCBrowseServerAddressSpaceDisp::SetItemIDEnumerator Method

ODL Syntax

HRESULT SetItemIDEnumerator(	[in] Long BrowseFilterType,
[in] BSTR FilterCriteria,
[in] short DataTypeFilter, 
[in] long AccessRightsFilter);

VB Syntax

Dim Svr as IOPCServerBrowseServerAddressSpaceDisp

Set Svr = CreateObject(“OPCVendorX_Server.1”)
Svr.SetItemIDEnumerator OPC_FLAT, “*”, VT_I4, OPC_ACCESS_READ

Description

Sets the type of enumerator to use when an enumerator is requested via _NewEnum.  The position from the which the browse is done can be set via ChangeBrowsePosition.

Return Value

None

parameters

BrowseFilterType

OPC_BRANCH -	returns only items that have children

OPC_LEAF -	returns only items that don’t have children

OPC_FLAT -	returns everything at and below this level including all children of children - basically ‘pretends’ that the address space in actually FLAT  This parameter is ignored for FLAT address space.

FilterCriteria
A server specific filter string.  This is entirely free format and should be entered by the user via an EDIT field.  Support for some form of regular expressions (e.g. wild card as ‘*’) is recommended but not required.  A NUL string indicates no filtering.

DataTypeFilter
Filter the returned list based in the available datatypes (those that would succeed if passed to AddItem).  VT_EMPTY indicates no filtering.

AccessRightsFilter
Filter based on the AccessRights bit mask (OPC_ACCESS_READ or OPC_ACCESS_WRITE).  0 indicates no filtering.

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_INVALIDARG | An Invalid Parameter was Passed. |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

Note that the strings returned by the enumerator represent the BRANCHs and LEAFS contained in the current level.  They do not include any delimiters.  Also it is allowed for the Server to return a ‘hint’ string rather than an actual legal Item ID.  For example a PLC with 32000 registers could return a single string of “0 to 31999” rather than return 32,000 individual strings.  For this reason (as well as the fact that browser support is optional) clients should always be prepared to allow manual entry of ITEM ID strings.

Clients are allowed to get and hold Enumerators for more than one ‘browse position’ at a time.

Changing the browse position will not affect any enumerator the client already has.

The client must Release each Enumerator when he is done with it.

#### IOPCBrowseServerAddressSpaceDisp:: GetItemIDString Method

ODL Syntax

HRESULT GetItemIDString(	[in] BSTR ItemDataID,
	[out, retval] BSTR *ItemID);

VB Syntax

Dim Svr as IOPCServerBrowseServerAddressSpaceDisp
Dim ItemID as string

Set Svr = CreateObject(“OPCVendorX_Server.1”)
ItemID = Svr.GetItemIDString(“*”)

Description

Provides a way to assemble a ‘fully qualified’ ITEM ID in a hierarchical space.  This is required since at each point one is browsing just the names ‘below’ the current node.

Return Value

ItemID
Item ID string

parameters

ItemDataID
The name of a BRANCH or LEAF at the current level.

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_INVALIDARG | An Invalid Parameter was Passed. |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

It is possible that a server could support hierarchical browsing of an address space that contains globally unique tags.  For example in the case of AREA1.REACTOR5.TIC101, the tag TIC101 might still be globally unique and might therefore be acceptable to AddItem.  However the expected behavior is that (a) GetItemID will always return the fully qualified name and (b) that the server will always accept (even if it does not require) the fully qualified name.

This function need not be called for a FLAT space.  However if it is then it will simply return the same string that was passed in.

It is valid to form an ItemID that represents a BRANCH.  This could happen if you pass a BRANCH rather than a LEAF.  The resulting string might fail if passed to AddItem (but would work if passed to SetInitialPosition).

The client must free the returned string.

#### IOPCBrowseServerAddressSpaceDisp:: SetAccessPathEnumerator Method

ODL Syntax

HRESULT SetAccessPathEnumerator([in] BSTR ItemID);

VB Syntax

Dim Svr as IOPCServerBrowseServerAddressSpaceDisp

Set Svr = CreateObject(“OPCVendorX_Server.1”)
Svr.SetAccessPathEnumerator “*”

Description

Sets the type of enumerator to use when an enumerator is requested via _NewEnum. It provides a way to browse the available AccessPaths for an ITEM ID.

Return Value

None

parameters

ItemID
Fully Qualified ItemID.

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_INVALIDARG | An Invalid Parameter was Passed. |
| E_OUTOFMEMORY | Not enough memory |
| E_NOTIMPL | The server does not require or support access paths. |
| E_FAIL | The function was unsuccessful. |

Comments

Clients are allowed to get Access Path Enumerators for more than one item at a time.

Changing the browse position will not affect any enumerator the client already has.

The client must Release each Enumerator when it is done with it.

## OPCGroup

The OPCGroup object is the object that an OPC server delivers to manage a collection of items. The interfaces for this object are discussed in the following sections.

### IOPCItemMgtDisp Interface

This interface to the OPCServer Object allows a client to add, remove and control the behavior of items in a group.

#### IOPCItemMgtDisp:: Count Property

ODL Syntax

[
	propget
]
	HRESULT Count([out, retval] long * pCount);

VB Syntax

Dim Grp as IOPCItemMgtDisp
Dim Count as Integer
…
Count=Grp.Count
MsgBox “There are “ & Count & “Items defined”

VB Syntax

Count () As Long

Description

Returns the number of items in the collection. Read-only property

Return Value

pCount
The number of items in the collection.

parameters

None

Comments

The term ‘Item’ in this context is a VB term which represents an item in an automation collection..  It has no relation to OPC Items.

#### IOPCItemMgtDisp:: _NewEnum Property

ODL Syntax

[
	propget, 
	restricted,
	id( DISPID_NEWENUM )
]
	HRESULT _NewEnum([out, retval] IUnknown ** ppUnk);

VB Syntax

Dim Grp as IOPCItemMgtDisp
Dim Val as Variant

…
For Each Val in Grp
	MsgBox Val
Next Val

Description

Returns an enumerator that supports IEnumVariant for the items currently in the collection. Read-only property.

Return Value

ppUnk
The enumerator object.

parameters

None

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

#### IOPCItemMgtDisp::Item Method

ODL Syntax

HRESULT Item(	[in] VARIANT ItemSpecifier, 
			[out, retval] IDispatch ** ppDisp);

VB Syntax

Dim Grp as IOPCItemMgtDisp
Dim Item as Object
Dim Item2 as Object

…
Set Item = Grp.Item(1)

Set Item2 = Grp.Item(“ItemID”)

Description

Special method used by Automation to implement the FOR/NEXT feature of Basic.

Return Value

ppUnk
An IDISPATCH for an OPC Item Object. Returns VT_EMPTY if the Item is not found.

parameters

None

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_INVALIDARG | An Invalid Parameter was Passed. |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

The term ‘Item’ in this context is a VB term which represents an item in an automation collection..  It has no relation to OPC Items.

#### IOPCItemMgtDisp:: AddItems Method

ODL Syntax

HRESULT AddItems(	[in] long NumItems,
	[in] VARIANT ItemIDs,
	[in] VARIANT ActiveStates,
	[in] VARIANT ClientHandles,
	[out] VARIANT * pServerHandles,
	[out] VARIANT * pErrors,
	[out] VARIANT * pItemObjects,
	[in, optional] VARIANT AccessPaths,
	[in, optional] VARIANT RequestedDataTypes,
	[in, out, optional] VARIANT * pBlobs,
	[out, optional] VARIANT * pCanonicalDataTypes,
	[out, optional] VARIANT * pAccessRights);

VB Syntax

Dim Grp as IOPCItemMgtDisp
Dim ItemIDs(1) as String
Dim ClientHdls(1) as long
Dim ServerHdls, Errors, ItemObjects as Variant
ItemIDs(0)=”*”
ClientHdls(0)=1

…
Grp.AddItems 1, ItemIDs, TRUE, ClientHdls, ServerHdls, Errors, ItemObjects

Description

Add one or more items to a  group.

Return Value

None.

parameters

NumItems
The number of items to be added

ItemIDs
An array of Item identifiers. A null-terminated string that uniquely identifies an OPC data item.

ActiveStates
An array of Boolean values that indicate whether the item should be added to the Group in the active or inactive state.

ClientHandles
An array of handles (long) the client wishes to use to reference the Item

pServerHandles
An array of handles (long) the server assigned to the Items being added to the Group.

pErrors
An array of HRESULTS (long). This tells the client which of the items was successfully added. For any item  which failed it provides a reason.

pItemObjects
An array of Item objects returned as a result of the AddItems method

AccessPaths
An array containing the access paths (string) that the server should associate with each item added

RequestedDataTypes
An array of data types (integer) requested for each Item by the client.

pBlobs
An array of pointers to the Blobs for each Item added. (see discussion on Blobs)

pCanonicalDataTypes
An array of the native data type (integer) for each Item added.

pAccessRights
An array of AccessRights (integer). Indicates if the Items are read only, write only, or read/write.

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| S_FALSE | The function was partially successful. See the pErrors to determine what happened |
| OPC_E_PUBLIC | Cannot add items to a public group |
| E_INVALIDARG | An Invalid Parameter was Passed. |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

It is legal to add the same item to the group more than once. Doing so will in fact generate a 2nd item with a unique ServerHandle.

The server provided item handle will be unique within the group but may not be unique across groups. The server is allowed to ‘reuse’ the handles of deleted items.

Items cannot be added to public groups.

#### IOPCItemMgtDisp:: ValidateItems Method

ODL Syntax

HRESULT ValidateItems(	[in] long NumItems,
[in] VARIANT ItemIDs,
[out] VARIANT * pErrors,
[in, optional] VARIANT AccessPaths,
[in, optional] VARIANT RequestedDataTypes,
[in, optional] VARIANT BlobUpdate,
[in, out, optional] VARIANT * pBlobs,
[out, optional] VARIANT * pCanonicalDataTypes,
[out, optional] VARIANT * pAccessRights);

VB Syntax

Dim Grp as IOPCItemMgtDisp
Dim ItemIDs(1) as String
Dim ServerHdls, Errors, ItemObjects as Variant
ItemIDs(0)=”*”

…
Grp.ValidateItems 1, ItemIDs, Errors

Description

Determines if an item is valid (could it be added without error). Also returns information about the item such as canonical datatype. Does not affect the group in any way.

Return Value

None.

parameters

NumItems
The number of items to be added

ItemIDs
An array of Item identifiers. A null-terminated string that uniquely identifies an OPC data item.

pErrors
An array of HRESULTS (long). This tells the client which of the items was successfully added. For any item which failed it provides a reason.

AccessPaths
An array containing the access path (string) that the server should associate with each item added

RequestedDataTypes
An array of data types (integer) requested for each Item by the client

BlobUpdate
A variant containing a boolean telling the server whether or not update the blob.

pBlobs
An array of pointers to the Blobs for each Item added. (see discussion on Blobs)

pCanonicalDataTypes
An array of the native data type (integer) for each Item added.

pAccessRights
An array of AccessRights (integer). Indicates if the Items are read only, write only, or read/write

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_INVALIDARG | An Invalid Parameter was Passed. |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

#### IOPCItemMgtDisp:: RemoveItems Method

ODL Syntax

HRESULT RemoveItems(	[in] long NumItems,
[in] VARIANT ServerHandles,
[out] VARIANT * pErrors,
[in] boolean Force);

VB Syntax

Dim Grp as IOPCItemMgtDisp
Dim ServerHandles(1) as long
Dim Errors as Variant
ServerHandles(0)=1

…
Grp.RemoveItems 1, ServerHandles, Errors, FALSE

Description

Removes (deletes) items from a group. Basically this is the reverse of AddItems.

Return Value

None.

parameters

NumItems
Number of items to be removed.

ServerHandles
Array of server items handles (long). These were returned from AddItem.

pErrors
Array of HRESULTs (long). Indicates which items were successfully removed.

Force
Forces deletion of the Item even if references are outstanding.

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_INVALIDARG | An Invalid Parameter was Passed. |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

Note that adding and removing items from a group does not affect the address space of the server or physical device. It simply indicates whether or not the client is interested in those particular items.

Items cannot be removed from a public group.

#### IOPCItemMgtDisp:: SetActiveState Method

ODL Syntax

HRESULT SetActiveState(	[in] long NumItems,
[in] VARIANT ServerHandles,
[in] boolean ActiveState,
[out] VARIANT * pErrors);

VB Syntax

Dim Grp as IOPCItemMgtDisp
Dim ServerHandles(1) as long
Dim Errors as Variant
ServerHandles(0)=1

…
Grp.SetActiveState 1, ServerHandles, TRUE, Errors

Description

Sets one or more items in a group to active or inactive. This controls whether or not valid data can be obtained from Read CACHE for those items and whether or not they are included in the IAdvise subscription to the group.

Return Value

None.

parameters

NumItems
The number of items to be affected.

ServerHandles
Array of Server items handles (long).

ActiveState
TRUE if items are to be activated. FALSE if items are to be deactivated.

pErrors
Array of HRESULTS. Indicates which items were successfully affected.

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_INVALIDARG | An Invalid Parameter was Passed. |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

Deactivating items will not result in a callback (since by definition callbacks do not occur for inactive items).  Activating items will result in an IAdvise callback.

#### IOPCItemMgtDisp:: SetClientHandles Method

ODL Syntax

HRESULT SetClientHandles(	[in] long NumItems,
						[in] VARIANT ServerHandles,
						[in] VARIANT ClientHandles,
						[out] VARIANT * pErrors);

VB Syntax

Dim Grp as IOPCItemMgtDisp
Dim ServerHandles(1) as long
Dim ClientHandles(1) as long
Dim Errors as Variant
ServerHandles(0)=1
ClientHandles(0)=2

…
Grp.SetClientHandles 1, ServerHandles, ClientHandles, Errors

Description

Changes the client handle for one or more items in a group.

Return Value

None.

parameters

NumItems
The number of items to be affected.

ServerHandles
Array of Server items handles (long).

ClientHandles
Array of new Client item handles (long) to be stored.

pErrors
Array of HRESULTS. Indicates which items were successfully affected.

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_INVALIDARG | An Invalid Parameter was Passed. |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

In general, it is expected that clients will set the client handle when the item is added and not change it later.

Behavior

The behavior of this standard assumes that the client handles are unique with respect to each client. It is expected that a client will assign unique value to the client handle if they intend on using any of the asynchronous functions of the OPC interfaces, including IOPCAsyncIO, and IDataObject/IAdviseSink interfaces, since this is the only key to the information that the server provides to the client with the data that is provided as a result of the IOPCAsyncIO, and IDataObject/IAdviseSink interfaces.

#### IOPCItemMgtDisp:: SetDataTypes Method

ODL Syntax

HRESULT SetDatatypes(	[in] long NumItems,
					[in] VARIANT ServerHandles,
					[in] VARIANT RequestedDataTypes,
					[out] VARIANT * pErrors);

VB Syntax

Dim Grp as IOPCItemMgtDisp
Dim ServerHandles(1) as long
Dim RequestedDataTypes(1) as integer
Dim Errors as Variant
ServerHandles(0)=1
RequestedDataTypes(0)=2

…
Grp.SetClientHandles 1, ServerHandles, RequestedDataTypes, Errors

Description

Changes the requested data type for one or more items in a group.

Return Value

None.

parameters

NumItems
The number of items to be affected.

ServerHandles
Array of Server items handles (long).

RequestedDataTypes
Array of new Requested Datatypes (integer) to be stored.

pErrors
Array of HRESULTS. Indicates which items were successfully affected.

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_INVALIDARG | An Invalid Parameter was Passed. |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

In general, it is expected that clients will set the requested datatype when the item is added and not change it later. This function is most useful for setting the datatype for items in a public group to which the client has connected.

### OPCGroup as IOPCGroupStateMgtDisp

This interface to the OPCServer Object allows the client to manage the overall state of the group. Primarily this allows changes to the update rate and active state of the group.

#### IOPCGroupStateMgtDisp:: ActiveStatus Property

ODL Syntax

[
	propget
]
	HRESULT ActiveStatus([out, retval] boolean * pActiveStatus);

[
	propput
]
	HRESULT ActiveStatus([in] boolean ActiveStatus);

VB Syntax

Dim Grp as IOPCGroupStateMgtDisp
Dim ActiveStatus as boolean
…
ActiveStatus = Grp.ActiveStatus
Grp.ActiveStatus = FALSE

Description

This property is used to obtain the current status of a Group (active/inactive) or to set a Group active or inactive.

Return Value(PropGet)

pActiveStatus
The current status of a Group (active/inactive)

parameters(PropGet)

None

Return Value(PropPUT)

None

parameters(PropPUT)

ActiveStatus
The status of a Group (active/inactive) to be set.

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_INVALIDARG | An Invalid Parameter was Passed. |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

#### IOPCGroupStateMgtDisp:: ClientGroupHandle Property

ODL Syntax

[
	propget
]
	HRESULT ClientGroupHandle([out, retval] long * phClientGroupHandle);

[
	propput
]
	HRESULT ClientGroupHandle([in] long ClientGroupHandle);

VB Syntax

Dim Grp as IOPCGroupStateMgtDisp
Dim ClientGroupHandle as long
…
ClientGroupHandle = Grp.ClientGroupHandle
Grp. ClientGroupHandle = 1

Description

This property allows the client to retrieve or set the current ClientHandle for the Group.

Return Value(PropGet)

phClientGroupHandle
The current ClientHandle for the Group)

parameters(PropGet)

None

Return Value(PropPUT)

None

parameters(PropPUT)

ClientGroupHandle
The ClientHandle for the Group.

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_INVALIDARG | An Invalid Parameter was Passed. |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

#### IOPCGroupStateMgtDisp:: ServerGroupHandle Property

ODL Syntax

[
	propget
]
	HRESULT ServerGroupHandle([out, retval] long * phServerGroupHandle);

VB Syntax

Dim Grp as IOPCGroupStateMgtDisp
Dim ServerGroupHandle as long
…
ServerGroupHandle = Grp.ClientGroupHandle

Description

This property returns the ServerGroupHandle for the Group.

Return Value

phServerGroupHandle
The current ServerGroupHandle for the Group)

parameters

None

Function Return Type

VT_I4

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

#### IOPCGroupStateMgtDisp:: Name Property

ODL Syntax

[
	propget
]
	HRESULT Name([out, retval] BSTR * pName);

[
	propput
]
	HRESULT Name([in] BSTR Name);

VB Syntax

Dim Grp as IOPCGroupStateMgtDisp
Dim Name as BSTR
…
Name = Grp.Name
Grp.Name = “*”

Description

This property obtains or sets the Group name.

Return Value(PropGet)

pName
The current group name for the Group)

parameters(PropGet)

None

Return Value(PropPUT)

None

parameters(PropPUT)

Name
The group name for the Group.

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

#### IOPCGroupStateMgtDisp:: UpdateRate Property

ODL Syntax

[
	propget
]
	HRESULT UpdateRate([out, retval] long * pUpdateRate);

[
	propput
]
	HRESULT UpdateRate([in] long UpdateRate);

VB Syntax

Dim Grp as IOPCGroupStateMgtDisp
Dim UpdateRate as long
…
UpdateRate = Grp.UpdateRate
Grp.UpdateRate = 1000

Description

This property returns the current UpdateRate or set the UpdateRate for the Group.

Return Value(PropGet)

pUpdateRate
The current UpdateRate for the Group)

parameters(PropGet)

None

Return Value(PropPUT)

None

parameters(PropPUT)

UpdateRate
The UpdateRate for the Group.

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_INVALIDARG | An Invalid Parameter was Passed. |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

#### IOPCGroupStateMgtDisp:: TimeBias Property

ODL Syntax

[
	propget
]
	HRESULT TimeBias([out, retval] long * pTimeBias);

[
	propput
]
	HRESULT TimeBias([in] long TimeBias);

VB Syntax

Dim Grp as IOPCGroupStateMgtDisp
Dim TimeBias as long
…
TimeBias = Grp.TimeBias
Grp.TimeBias = 0

Description

This property returns the current TimeBias or sets a new TimeBias for the Group.

Return Value(PropGet)

pTimeBias
The current TimeBias for the Group)

parameters(PropGet)

None

Return Value(PropPUT)

None

parameters(PropPUT)

TimeBias
The TimeBias for the Group.

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_INVALIDARG | An Invalid Parameter was Passed. |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

#### IOPCGroupStateMgtDisp:: PercentDeadBand Property

ODL Syntax

[
	propget
]
	HRESULT PercentDeadBand([out, retval] float * pPercentDeadBand);
[
	propget
]
	HRESULT PercentDeadBand([in] float PercentDeadBand);

VB Syntax

Dim Grp as IOPCGroupStateMgtDisp
Dim PercentDeadBand as single
…
PercentDeadBand = Grp.PercentDeadBand
Grp.PercentDeadBand = OPC_NOEU

Description

This property returns the percent change in an item value that will cause an exception report of that value to a client.

Return Value(PropGet)

pPercentDeadBand
The percent change in an item value that will cause an exception report of that value to a client. This parameter only applies to items in the group that have dwEUType of Analog. [See discussion of Percent Deadband in Section 4.4.1].

parameters(PropGet)

None

Return Value(PropPUT)

None

parameters(PropPUT)

PercentDeadBand
The percent change in an item value that will cause an exception report of that value to a client. This parameter only applies to items in the group that have dwEUType of Analog. [See discussion of Percent Deadband in Section 4.4.1].

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_INVALIDARG | An Invalid Parameter was Passed. |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

#### IOPCGroupStateMgtDisp:: LCID Property

ODL Syntax

[
	propget
]
	HRESULT LCID([out, retval] long * pLCID);

[
	propput
]
	HRESULT LCID([in] long LCID);

VB Syntax

Dim Grp as IOPCGroupStateMgtDisp
Dim LCID as long
…
LCID = Grp.LCID
Grp.LCID = &H0904

Description

This property returns the language to be used by the server when returning values.

Return Value(PropGet)

pLCID
The language to be used by the server when returning values (including EU enumeration’s) as text for operations on this group. This could also include such things as alarm or status conditions or digital contact states.

parameters(PropGet)

None

Return Value(PropPUT)

None

parameters(PropPUT)

LCID
The language to be used by the server when returning values (including EU enumeration’s) as text for operations on this group. This could also include such things as alarm or status conditions or digital contact states.

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_INVALIDARG | An Invalid Parameter was Passed. |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

#### IOPCGroupStateMgtDisp:: CloneGroup Method

ODL Syntax

HRESULT CloneGroup(		[in, optional] VARIANT Name,
					[out, retval] IDispatch ** ppDisp);

VB Syntax

Dim Grp as IOPCGroupStateMgtDisp
Dim NewGroup as Object
…
Set NewGroup = Grp.CloneGroup “*”

Description

Create a second copy of a group. As noted elsewhere the name must be unique. This works for both public and private groups. However, the new group is always a private group. Most of the group and item properties are duplicated. The exceptions are:

Active Status of group is set to FALSE

A new ServerHandle for the group is produced.

Return Value

ppDisp
The new cloned group object

parameters

Name
Name for the new cloned group object

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_INVALIDARG | An Invalid Parameter was Passed. |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

### OPCGroup as IOPCSyncIODisp

IOPCSyncIODisp allows a client to perform synchronous read and write operations to a server. The operations will run to completion.

#### IOPCSyncIODisp:: OPCRead Method

ODL Syntax

HRESULT OPCRead(	[in] short Source,
				[in] long NumItems,
				[in] VARIANT ServerHandles,
				[out] VARIANT * pValues,
				[out, optional] VARIANT * pQualities,
				[out, optional] VARIANT * pTimeStamps,
				[out, optional] VARIANT * pErrors);

VB Syntax

Dim Grp as IOPCSyncIODisp
Dim ServerHandles(1) as long
Dim Values as Variant
ServerHandles(0)=1
 
…
Grp.OPCRead OPC_DS_CACHE, ServerHandles, Values

Description

This function reads the value, quality and timestamp information for one or more items in a group.  The function runs to completion before returning.  The data can be read from CACHE in which case it should be accurate to within the ‘UpdateRate’ of the group. The data can be read from the DEVICE in which case an actual read of the physical device is to be performed. The exact implementation of CACHE and DEVICE reads is not defined by this specification.

For CACHE reads the data is only valid if both the group and the item are active. Otherwise the Quality will indicate that the data is not valid.

DEVICE reads are not affected by the ACTIVE state of the group or item.

Return Value

None

parameters

Source
The ‘data source’; OPC_DS_CACHE or OPC_DS_DEVICE

NumItems
The number of items to be read.

ServerHandles
The list of server item handles (long) for the items to be read

pValues
Array of returned item values (variant).

pQualities
Array of returned item quality values (short).

pTimeStamps
Array of time stamps for the values (date).

pErrors
Array of HRESULTs (long) indicating the success of the individual item reads. The errors correspond to the handles passed in ServerHandles. This indicates whether the read succeeded in obtaining a defined value, quality and timestamp.  NOTE any FAILED error code indicates that the corresponding Value, Quality and Time stamp are UNDEFINED

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_INVALIDARG | An Invalid Parameter was Passed. |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

pErrors Return codes

| Return Code | Description |
| --- | --- |
| OPC_E_INVALIDHANDLE | One or more of the passed handles was invalid. The pError array indicates which handles in ServerHandles were invalid. NOTE that this is a FAIL code: if any handle is invalid this error is returned and the entire read operation is rejected. No callback will occur. |

Comments

Expected behavior is that a CACHE read should be completed very quickly (within milliseconds). A DEVICE read may take a very long time (many seconds or more). Note that depending on the details of the implementation (e.g. which threading model is used) the DEVICE read may also prevent any other operations from being performed on the server by any other clients.

For this reason Clients are expected to use CACHE reads in most cases. DEVICE reads are intended for ‘special’ circumstances such as diagnostics.

#### IOPCSyncIODisp:: OPCWrite Method

ODL Syntax

HRESULT OPCWrite(	[in] long NumItems,
				[in] VARIANT ServerHandles,
				[in] VARIANT Values,
				[out, optional] VARIANT * pErrors);

VB Syntax

Dim Grp as IOPCSyncIODisp
Dim ServerHandles(1) as long
Dim Values(1) as long
ServerHandles(0)=1
Values(0)=1
 
…
Grp.OPCWrite 1, ServerHandles, Values

Description

Writes values to one or more items in a group. The function runs to completion. The values are written to the DEVICE. That is the function should not return until it verifies that the device has actually accepted (or rejected) the data.

Writes are not affected by the ACTIVE state of the group or item.

Return Value

None

parameters

NumItems
Number of items to be written

ServerHandles
The list of server item handles for the items to be written

Values
List of values (variant) to be written to the items. The datatypes of the values do not need to match the datatypes of the target items. However an error will be returned if a conversion cannot be done.

pErrors
Array of HRESULTs (long) indicating the success of the individual item Writes. The errors correspond to the handles passed in phServer. This indicates whether the target device or system accepted the value.  NOTE any FAILED error code indicates that the value was rejected by the device.

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_INVALIDARG | An Invalid Parameter was Passed. |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

pErrors Return codes

| Return Code | Description |
| --- | --- |
| OPC_E_INVALIDHANDLE | One or more of the passed handles was invalid. The pError array indicates which handles in ServerHandles were invalid. NOTE that this is a FAIL code: if any handle is invalid this error is returned and the entire write operation is rejected. No callback will occur. |

Comments

A DEVICE write may take a very long time (many seconds or more). Note that depending on the details of the implementation (e.g. which threading model is used) the DEVICE write may also prevent any other operations from being performed on the server by any other clients.

For this reason Clients are expected to use ASYNC write rather than SYNC write in most cases.

### OPCGroup as IOPCASyncIODisp

This interface to the OPCServer Object allows a client to perform asynchronous read and write operations to a server. The operations will be ‘queued’ and the function will return immediately so that the client can continue to run. Each operation is treated as a ‘transaction’ and is assigned a transaction ID. As the operations are completed, a callback will be made to the IAdvise Sink in the client (if one has been established). The information in the callback will indicate the transaction ID and the error results.  By convention, 0 is an invalid transaction id.

#### IOPCASyncIODisp:: AddCallbackReference Method

ODL Syntax

HRESULT AddCallbackReference(	[in] long Context,
						[in] IDispatch * pCallback,
						[out, retval] long * pConnection);

VB Syntax

Dim Grp as IOPCASyncIODisp
Dim Connection as long
Dim CallBack as Object

…‘Assign a client defined callback object to CallBack
Connection = Grp.AddCallbackReference(OPC_WRITE_COMPLETED CallBack)

Description

This call tells the server which object to call back for asynchronous communication back to the client. The context tells the server what format to send the data in for this particular callback reference. The connection is a server assigned value that the client uses to terminate any future callbacks by passing it in DropCallbackReference.

Return Value

pConnection
The server assigned value the client will use to terminate the callbacks.

parameters

Context
Format the data should be returned in. This is either values; values and timestamps; or asynchronous write complete statuses.

pCallback
The object the server will call back into. For the methods in this object please refer to section: 3.4.

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_INVALIDARG | An Invalid Parameter was Passed. |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

#### IOPCASyncIODisp:: DropCallbackReference Method

ODL Syntax

HRESULT DropCallbackReference([in] long Connection);

VB Syntax

Dim Grp as IOPCASyncIODisp
Dim Connection as long
…
Grp.DropCallbackReference Connection

Description

This will terminate callback for the Connection specified.

Return Value

None

parameters

Connection
This value was returned by the server in the AddCallbackReference method. The client uses that value in this method to inform the server which callback reference to drop.

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_INVALIDARG | An Invalid Parameter was Passed. |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

#### IOPCASyncIODisp:: OPCRead Method

ODL Syntax

HRESULT OPCRead(	[in] short Source
				[in] long NumItems,
				[in] VARIANT ServerHandles,
				[out, optional] VARIANT * pErrors,
				[out, retval] long * pTransactionID)

VB Syntax

Dim Grp as IOPCASyncIODisp
Dim ServerHandles(1) as long
Dim TransactionID as long
ServerHandles(0)=1

…
TransactionID = Grp.OPCRead(OPC_DS_CACHE, 1, ServerHandles)

Description

Read one or more items in a group. The results are returned via the

Return Value

pTransactionID
Returns a server generated transaction ID.

parameters

Source
Data source: OPC_DS_CACHE or OPC_DS_DEVICE.

NumItems
Number of items to be read.

ServerHandles
Array of server item handles (long) of the items to be read.

pErrors
Array of errors (long) for each item - returned by the server. Indicates only if the corresponding server handle was valid.

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_INVALIDARG | An Invalid Parameter was Passed. |
| OPC_E_INVALIDHANDLE | One or more of the passed handles was invalid. The pError array indicates which handles in ServerHandles were invalid. NOTE that this is a FAIL code: if any handle is invalid this error is returned and the entire read operation is rejected. No callback will occur. |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

If the passed handles are valid and the operation is performed then all item level error returns will be via OnDataChange.  These error codes have the same values as those returned by IOPCSyncIO::Read.

NOTE: all of the results must be returned in a single callback.  As an implementation note, if the items in the group require multiple physical transactions to one or more physical devices then the server must wait until all of them are complete before invoking OnDataChange.

#### IOPCASyncIODisp:: OPCWrite Method

ODL Syntax

HRESULT OPCWrite(	[in] long NumItems,
				[in] VARIANT ServerHandles,
				[in] VARIANT Values,
				[out, optional] VARIANT * pErrors
				[out, retval] long * pTransactionID);

VB Syntax

Dim Grp as IOPCASyncIODisp
Dim ServerHandles(1) as long
Dim Values(1) as integer
Dim TransactionID as long
ServerHandles(0)=1
Values(0)=2

…
TransactionID = Grp.OPCWrite(1, ServerHandles, Values)

Description

Write one or more items in a group. The results are returned via the

Return Value

pTransactionID
Returns a server generated transaction ID.

parameters

NumItems
Number of items to be written.

ServerHandles
List of server items handles (long) for the items to be written.

Values
List of values (variant) to be written. The value data types do not match the requested or canonical item datatype but must be ‘convertible’ to the canonical type.

pErrors
Array of errors (long) for each item returned by the server. Indicates only whether the corresponding server handle was valid.

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| OPC_E_INVALIDHANDLE | One or more of the passed handles was invalid. The pError array indicates which handles in ServerHandles were invalid. NOTE that this is a FAIL code: if any handle is invalid this error is returned and the entire write operation is rejected. No callback will occur. |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

If the passed handles are valid and the operation is performed then all item level error returns will be via OnDataChange.  These error codes have the same values as those returned by IOPCSyncIO::Write.

NOTE: all of the results must be returned in a single callback.  As an implementation note, if the items in the group require multiple physical transactions to one or more physical devices then the server must wait until all of them are complete before invoking OnDataChange.

#### IOPCASyncIODisp:: Cancel Method

ODL Syntax

HRESULT Cancel([in] long TransactionID);

VB Syntax

Dim Grp as IOPCASyncIODisp
Dim TransactionID as long

…
Grp.Cancel TransactionID

Description

Request that the server cancel an outstanding transaction.

Return Value

None

parameters

TransactionID
The TransactionID to be canceled.

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_INVALIDARG | An Invalid Parameter was Passed. |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

The exact behavior (for example whether an operation that has actually started will be aborted) will be server specific and will also depend on the timing of the cancel request.  Also, depending on the timing, a Callback for the transaction may or may not occur.  This method is intended to be used during shutdown of a task.

#### IOPCASyncIODisp:: Refresh Method

ODL Syntax

HRESULT Refresh(	[in] short Source
				[out, retval] long * pTransactionID);

VB Syntax

Dim Grp as IOPCASyncIODisp
Dim TransactionID as long

…
TransactionID = Grp.Refresh(OPC_DS_CACHE)

Description

Force a callback for all active items in the group.

Return Value

pTransactionID
Returns a server generated transaction ID. This is included in the ‘completion’ information provided to the IAdvise.

parameters

Source
Data source OPC_DS_CACHE or OPC_DS_DEVICE.

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_INVALIDARG | An Invalid Parameter was Passed. |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

### OPCGroup as IOPCPublicGroupStateMgtDisp

This optional interface to the OPCServer Object is used to convert a private group to a public group. Servers optionally provide this interface on group objects. Note that a group created by a client is always created initially as a private group. This interface can be obtained from that private group in order to convert the group to a public group.

#### IOPCPublicGroupStateMgtDisp:: State Property

ODL Syntax

[
	propget
]
	HRESULT State([out, retval] boolean * pPublic);

VB Syntax

Dim Grp as IOPCPublicGroupStateMgtDisp
Dim GroupState as boolean

…
GroupState = Grp.State

Description

Returns the current state of the Group (public or private)

Return Value

pPublic
The current state of the Group (public or private).

parameters

None

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

#### IOPCPublicGroupStateMgtDisp:: MoveToPublic Method

ODL Syntax

HRESULT MoveToPublic(void);

VB Syntax

Dim Grp as IOPCPublicGroupStateMgtDisp

…
Grp.MoveToPublic

Description

Converts a private group to a public group. The group must have a name which must be unique among all existing public groups. The state of the group (active, UpdateRate, IAdvise connections, etc.) for the client is not affected.

Return Value

None

parameters

None

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

A public group cannot be converted back to a private group. However it can be ‘cloned’ into a new private group.

For public groups, the update rate, client group handle and active status are maintained as ‘instance’ data for each client.

For the items in the group the client handle, active status and requested data type are maintained as ‘instance’ data for each client.

Behavior

The behavior of this standard assumes that the client handles are unique with respect to each client. It is expected that a client will assign unique value to the client handle if they intend on using any of the asynchronous functions of the OPC interfaces, including IOPCAsyncIO, and IDataObject/IAdviseSink interfaces, since this is the only key to the information that the server provides to the client with the data that is provided as a result of the IOPCAsyncIO, and IDataObject/IAdviseSink interfaces.

## OPCItem Object

### OPCItem as IOPCItemDisp

This interface to the OPCItem Object provides properties and methods on the Item object.

#### IOPCItemDisp:: AccessPath Property

ODL Syntax

[
	propget
]
	HRESULT AccessPath([out, retval] BSTR * pAccessPath);

VB Syntax

Dim Itm as IOPCItemDisp
Dim AccessPath as String
…
AccessPath = Itm.AccessPath

Description

This property returns the AccessPath set for this Item.

Return Value

pAccessPath
The AccessPath set for this Item.

parameters

None

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

#### IOPCItemDisp:: AccessRights Property

ODL Syntax

[
	propget
]
	HRESULT AccessRights([out, retval] long * pAccessRights);

VB Syntax

Dim Itm as IOPCItemDisp
Dim AccessRights as long
…
AccessRights = Itm.AccessRights

Description

This property returns the AccessRights configured for this Item.

Return Value

pAccessRights
The AccessRights for this Item.

parameters

None

Function Return Type

VT_I4

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

#### IOPCItemDisp:: ActiveStatus Property

ODL Syntax

[
	propget
]
	HRESULT ActiveStatus([out, retval] boolean * pActiveStatus);
[
	propput
]
	HRESULT ActiveStatus([in] boolean ActiveStatus);

VB Syntax

Dim Itm as IOPCItemDisp
Dim ActiveStatus as boolean
…
ActiveStatus = Itm.ActiveStatus
Itm.ActiveStatus = TRUE

Description

This property allows the client application to read or set the current ActiveStatus (active/inactive) for the Item.

Return Value(PropGet)

pActiveStatus
The current ActiveStatus (active/inactive) for the Item.

parameters(PropGet)

None

Return Value(PropPUT)

None

parameters(PropPUT)

ActiveStatus
The ActiveStatus (active/inactive) for the Item.

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_INVALIDARG | An Invalid Parameter was Passed. |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

#### IOPCItemDisp:: Blob Property

ODL Syntax

[
	propget
]
	HRESULT Blob([out, retval] VARIANT * pBlob);

VB Syntax

Dim Itm as IOPCItemDisp
Dim Blob as Variant
…
Blob = Itm.Blob

Description

This property returns the value for the Blob set for this Item.

Return Value)

pBlob
The value for the Blob set for this Item.

parameters

None

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

#### IOPCItemDisp:: ClientHandle Property

ODL Syntax

[
	propget
]
	HRESULT ClientHandle([out, retval] long * phClient);
[
	propput
]
	HRESULT ClientHandle([in] long Client);

VB Syntax

Dim Itm as IOPCItemDisp
Dim ClientHandle as long
…
ClientHandle = Itm.ClientHandle
Itm.ClientHandle = 1

Description

This property allows a client application to read or set the current ClientHandle for the Item.

Return Value(PropGet)

phClient
The current ClientHandle for the Item.

parameters(PropGet)

None

Return Value(PropPUT)

None

parameters(PropPUT)

Client
The ClientHandle for the Item.

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_INVALIDARG | An Invalid Parameter was Passed. |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

#### IOPCItemDisp:: ItemID Property

ODL Syntax

[
	propget
]
	HRESULT ItemID([out, retval] BSTR * pItemID);

VB Syntax

Dim Itm as IOPCItemDisp
Dim ItemID as BSTR
…
ItemID = Itm.ItemID

Description

This property returns the current ItemID configured for the Item.

Return Value

pItemID
The current ItemID for the Item.

parameters

None

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

#### IOPCItemDisp:: ServerHandle Property

ODL Syntax

[
	propget
]
	HRESULT ServerHandle([out, retval] long * pServer);

VB Syntax

Dim Itm as IOPCItemDisp
Dim ServerHandle as long
…
ServerHandle = Itm.ServerHandle

Description

This property returns the current ServerHandle for the Item.

Return Value

pServer
The current ServerHandle for the Item.

parameters

None

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

#### IOPCItemDisp:: RequestedDataType Property

ODL Syntax

[
	propget
]
	HRESULT RequestedDataType([out, retval] short * pRequestedDataType);
[
	propput
]
	HRESULT RequestedDataType([in] short RequestedDataType);

VB Syntax

Dim Itm as IOPCItemDisp
Dim RequestedDataType as short
…
RequestedDataType = Itm.RequestedDataType
Itm.RequestedDataType = VT_I4

Description

This property returns or allows the client application to set the current RequestedDataType configured for the Item.

Return Value(PropGet)

pRequestedDataType
The current RequestedDataType for the Item.

parameters(PropGet)

None

Return Value(PropPUT)

None

parameters(PropPUT)

RequestedDataType
The RequestedDataType for the Item.

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_INVALIDARG | An Invalid Parameter was Passed. |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

#### IOPCItemDisp:: Value Property

ODL Syntax

[
	propget
]
	HRESULT Value([out, retval] VARIANT * pValue);
[
	propput
]
	HRESULT Value([in] VARIANT NewValue);

VB Syntax

Dim Itm as IOPCItemDisp
Dim NewValue as VARIANT
…
NewValue = Itm.Value
Itm.Value = 1

Description

This property allows a client application to read or write the value for an Item.

Return Value(PropGet)

pValue
The current value for the Item.

parameters(PropGet)

None

Return Value(PropPUT)

None

parameters(PropPUT)

NewValue
The value for the Item.

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_INVALIDARG | An Invalid Parameter was Passed. |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

#### IOPCItemDisp:: Quality Property

ODL Syntax

[
	propget
]
	HRESULT Quality([out, retval] short * pQuality);

VB Syntax

Dim Itm as IOPCItemDisp
Dim Quality as short
…
Quality = Itm.Quality

Description

This property returns the current quality flag for the current Item value.

Return Value(PropGet)

pQuality
The current quality flag for the Item.

parameters(PropGet)

None

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

#### IOPCItemDisp:: TimeStamp Property

ODL Syntax

[
	propget
]
	HRESULT Timestamp([out, retval] DATE * pTimeStamp);

VB Syntax

Dim Itm as IOPCItemDisp
Dim Timestamp as DATE
…
Timestamp = Itm.Timestamp

Description

This property returns the time stamp for the Item value.

Return Value(PropGet)

pTimeStamp
The current time stamp for the Item.

parameters(PropGet)

None

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

#### IOPCItemDisp:: ReadError Property

ODL Syntax

[
	propget
]
	HRESULT ReadError([out, retval] long * pError);

VB Syntax

Dim Itm as IOPCItemDisp
Dim ReadError as long
…
ReadError = Itm.ReadError

Description

This property returns the last error that occurred during an Item read operation.

Return Value(PropGet)

pError
The last error that occurred during an Item read operation.

parameters(PropGet)

None

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

#### IOPCItemDisp:: EUType Property

ODL Syntax

[
	propget
]
	HRESULT EUType([out, retval] short * pEUType);

VB Syntax

Dim Itm as IOPCItemDisp
Dim EUType as short
…
EUType = Itm.pEUType

Description

This property returns the type of Engineering Units(EU) information contained in EUInfo property.

Return Value(PropGet)

pEUType
The type of Engineering Units(EU) information contained in EUInfo property.

parameters(PropGet)

None

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

#### IOPCItemDisp:: EUInfo Property

ODL Syntax

[
	propget
]
	HRESULT EUInfo([out, retval] VARIANT * pEUInfo);

VB Syntax

Dim Itm as IOPCItemDisp
Dim EUInfo as Variant
…
EUInfo = Itm.EUInfo

Description

This property returns the EU information.

Return Value(PropGet)

EUInfo
The EU information.

parameters(PropGet)

None

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

#### IOPCItemDisp:: WriteError Property

ODL Syntax

[
	propget
]
	HRESULT WriteError([out, retval] long * pError);

VB Syntax

Dim Itm as IOPCItemDisp
Dim WriteError as long
…
WriteError = Itm.WriteError

Description

This property returns the last error that occurred during an Item write operation.

Return Value(PropGet)

pError
The last error that occurred during an Item write operation.

parameters(PropGet)

None

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

#### IOPCItemDisp:: OPCRead Method

ODL Syntax

HRESULT OPCRead(	[in] short Source,
[out] VARIANT * pValue,
[out, optional] VARIANT * pQuality,
[out, optional] VARIANT * pTimeStamp);

VB Syntax

Dim Itm as IOPCItemDisp
Dim mValue as Variant
…
Itm.OPCRead OPC_DS_CACHE, mValue

Description

This function returns the value, quality flags, and timestamp for a particular item. Optionally, the source (cache or device) of the read may be specified.

Return Value

None

parameters

Source
Data source: OPC_DS_CACHE or OPC_DS_DEVICE

pValue
The data value for the Item.

pQuality
The quality (short) of this item.

pTimestamp
UTC TimeStamp (date) for this Item’s value.

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_INVALIDARG | An Invalid Parameter was Passed. |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

#### IOPCItemDisp:: OPCWrite Method

ODL Syntax

HRESULT OPCWrite([in] VARIANT NewValue);

VB Syntax

Dim Itm as IOPCItemDisp
Dim mValue as Variant
mValue=1
…
Itm.OPCWrite mValue

Description

This function writes a value to a device.

Return Value

None

parameters

Value
The value to be written to the device.

HRESULT Return Codes

| Return Code | Description |
| --- | --- |
| S_OK | The operation succeeded |
| E_INVALIDARG | An Invalid Parameter was Passed. |
| E_OUTOFMEMORY | Not enough memory |
| E_FAIL | The function was unsuccessful. |

Comments

## Exception and Asynchronous Notifications - Client Side

In order to be able to create a callback mechanism that will work with the OPC Automation Interface, the programmer must be using the Professional or Enterprise edition of Visual Basic Version 4.0 or higher.

To make a callback mechanism, create a Class Module in the application being developed. Define one of the two(or both) methods on the class with the following syntax:

Sub OnDataChange( GroupHandle as Long, Count as Long, ClientHandles() as Long, Values() as Variant, Qualities() as Long, GroupTime as Date, TimeStamps() as Date)

Return Value(PropGet)

None

parameters(PropGet)

GroupHandle
ClientHandle of group to which items belong.

Count
Number of Items in array.

ClientHandles
Array of client item handles.

Values
Array of client values.

Qualities
Array of client value qualities.

GroupTime
Time stamp of the group.

TimeStamps
Array of time stamps of the items.

Sub OnAsyncWriteComplete( GroupHandle as Long, Count as Long, CallbackHandles() as Long, ItemResults() as Long)

Return Value(PropGet)

None

parameters(PropGet)

GroupHandle
ClientHandle of group to which items belong.

Count
Number of Items in array.

ClientHandles
Array of client item handles.

ItemResults
Array of client value-writing-status.

In the application code, create an instance of your callback class using the following syntax:

Set CallbackObject = New ProjectName.CallbackClassName

After creating a group, the callback object can be added to or removed from a list of callback objects by using the method “IOPCAsyncIO::AddCallbackReference()” or “IOPCAsyncIO::DropCallbackReference()”. When the group is Active (On Scan) or the client is performing asynchronous operation, the callback method will receive notifications for all asynchronous operations and data change notifications on the group.

Please read the VB specificationation to learn how to add modules and methods, as well as create new instances of VB custom classes.

# Installation Issues

It is assumed that the server vendor will provide a SETUP.EXE to install the needed components for their server.  This will not be discussed further.  Other than the actual components, the main issue affecting OLE software is management of the Windows Registry.  The issues here are (a) what entries need to be made and (b) how they can be made.

## Registry Entries for Custom Interface

The following entries are the minimum required to support the Custom Interface for OPC Compliant Servers.

Required by all:

1. HKEY_CLASSES_ROOT\Vendor.Drivername.Version = A Description of your server

2. HKEY_CLASSES_ROOT\Vendor.Drivername.Version\CLSID = {Your Server’s unique CLSID}

3. HKEY_CLASSES_ROOT\Vendor.Drivername.Version\OPC

4. HKEY_CLASSES_ROOT\Vendor.Drivername.Version\OPC\Vendor =Your vendor name

5. HKEY_CLASSES_ROOT\CLSID\{Your Server’s unique CLSID} = A Description of your server

6. HKEY_CLASSES_ROOT\CLSID\{Your Server’s unique CLSID}\ProgID = Vendor.Drivername.Version

One or more of the following lines (inproc and/or local/remote and/or handler)

7. HKEY_CLASSES_ROOT\CLSID\{Your Server’s unique CLSID}\InprocServer32 = Full Path to DLL

8. HKEY_CLASSES_ROOT\CLSID\{YourServer’s unique CLSID}\LocalServer32 = Full Path to EXE

9. HKEY_CLASSES_ROOT\CLSID\{YourServer’s unique CLSID}\InprocHandler32 = Full Path to DLL

- Line 1 simply establishes your ProgID as a subkey of the ROOT under which other subkeys can be entered.  The description (the ‘value’ of this key) may be presented to the user as the name of an available OPC server (See example below).  It should match the description in line 5.

- The CLSID line (2) enables the CLSIDFromProgID function to work.  I.e. allows the system to open a key given the ProgID and obtain the CLSID as the value of that key.  See the example below.

- The OPC line (3) creates a ‘flag’ subkey that has no value but allows the client to easily browse for the available OPC servers (see the example below).  The fact that this subkey exists indicates that the corresponding ProgID (the parent key) is an OPC server.

- The Vendor line (4) is optional. It is simply a means of identifying all the vendors that have OPC servers registered on a particular machine.

- Line 5 simply establishes your CLSID as a subkey off of ROOT\CLSID under which the other subkeys can be entered.  The description (the ‘value’ of this key) should be a User Friendly description of the server.  It should match Item 1 above.

- The ProgID line (6) enables the ProgIDFromCLSID function to work.  I.e. allows the system to open a key given the CLSID and obtain the ProgID as the value of that key.  (This function is not commonly used).

- The InprocServer32 line (7) or LocalServer32 line (8) or InprocHandler32 line (9) allows CoCreateInstance to locate the DLL or EXE given the CLSID. The vendor should define at least one of these.

In general, self registration is recommended for servers to simplify installation.

Client Example: A typical custom interface client might use code like the following to list the user readable descriptions of the available OPC servers. The user could pick a Server and the client would then use the corresponding ProgID to obtain the CLSID to pass to CoCreateInstance:

hk = HKEY_CLASSES_ROOT;

for ( dwIndex = 0 ;

RegEnumKey( hk, dwIndex, szKey, MAX_KEYLEN) == ERROR_SUCCESS ;

++dwIndex )

{

// Open each subkey (the ProgIDs)

HKEY hProgID;

char szDummy[MAX_KEYLEN];

if (RegOpenKey( hk, szKey, &hProgID) == ERROR_SUCCESS)

{

// and for that subkey/ProgID - try to read the OPC Subkey

lVsize = MAX_KEYLEN;

if(RegQueryValue( hProgID, "OPC", szDummy, &lVsize) ==

ERROR_SUCCESS)

{

// And if it works then this is an OPC server...

// Show the Description to the user

lVsize = MAX_KEYLEN;

RegQueryValue( hk, (LPTSTR)szKey, szDesc, &lVsize) ;

printf("User Readable Description = %s\n", szDesc);

// (Show internal PROGID for testing/debug)

printf(" (KEY/Internal ProgID = %s)\n", szKey);

}

RegCloseKey( hProgID ) ;

}

// Enum the next one...

}

Now, having allowed the user to select a server, the client would use code like the following to get the CLSID to pass to CoCreateInstance.

// Get the CLSID from the ProgID

r1 = CLSIDFromProgID(szKey, &clsid);

if(FAILED(r1))

{

printf("CLSIDFromProgID failed for %ls\n", szName);

return NULL;

}

## Registry Entries for the Proxy/Stub DLL

The proxy/stub DLL is used for marshalling interfaces to LOCAL or REMOTE servers. It is generated directly from the IDL code and should be the same for every OPC Server. In general the Proxy/Stub will use self registration. (Define REGISTER_PROXY_DLL during the build). Since this is completely automatic and transparent it is not discussed further.

## Registry Entries for Automation Interface

In addition to the registry entries defined above, the registry entry for the Type Library  File (TLB) is required to support the Automation Interface.

HKEY_CLASSES_ROOT\TypeLib\{OPC Standard Defined GUID}\1.0\0\Win32 = Full Path to OPC Standard Type Library

HKEY_CLASSES_ROOT\TypeLib\{Vendor Defined GUID}\1.0\0\Win32 = Full Path to Vendor’s Type Library

All of the type library interfaces and the coclass definitions for the group and item objects are contained in the OPC Standard Type Library. Only the vendor specific coclass definition of the server object is needed in the vendor specific type library.

## Creating the Registry Entries

COM defines a “self-registration” mechanism that enables you to encapsulate registry needs into a DLL or EXE, providing clients and servers an easy way to make sure that any given module is fully and accurately registered.  In addition, COM also includes “unregistration” so that a server can remove all of its registry entries when the DLL or EXE is removed from the file system, thereby keeping the registry clean from useless entries.

When asked to self-register, a server must create all entries for every component that it supports, including any entries for type libraries.  When asked to “un-register” the server must remove those entries that it created in its self-registration.

For a DLL server, these requests are made through calls to the exported functions DllRegisterServer and DllUnregisterServer, which must exist in the DLL under these exact names.  Both functions take no arguments and return an HRESULT to indicate the result.  The two applicable error codes are SELFREG_E_CLASS (failure to register/unregister CLSID information) and SELFREG_E_TYPELIB (failure to register/unregister TypeLib information).

If the server is packaged in an EXE module, then the application wishing to register the server launches the EXE server with the command-line argument /RegServer or -RegServer (case-insensitive). If the application wishes to unregister the server, it launches the EXE with the command-line argument /UnregServer or -UnregServer. The self-registering EXE detects these command-line arguments and invokes the same operations as a DLL would within DllRegisterServer and DllUnregisterServer, respectively, registering its module path under LocalServer32 instead of InprocServer32 or InprocHandler32.

The server must register the full path to the installation location of the DLL or EXE module for their respective InprocServer32, InprocHandler32, and LocalServer32 keys in the registry. The module path is easily obtained through the Win32 API function GetModuleFileName.

The registry entries for proxy interfaces can be easily generated when compiling the proxy dll. Simply define the constant REGISTER_PROXY_DLL during compilation, and export DllRegisterServer and DllUnregisterServer during the link. One can now populate the registry by executing regsvr32 and passing the proxy dll name as an argument.

A registry file (.reg) can also be created to easily enter the CLSID information for your OPC server implementation. The following is an example (please try to uniquely name your server exe or dll):

REGEDIT

HKEY_CLASSES_ROOT\MyVendor.ServerName.1 = My OPC Server Description

HKEY_CLASSES_ROOT\MyVendor.ServerName.1\CLSID = { Your Server’s unique CLSID }

HKEY_CLASSES_ROOT\MyVendor.ServerName.1\OPC

HKEY_CLASSES_ROOT\MyVendor.ServerName.1\OPC\Vendor = My Vendor Name

HKEY_CLASSES_ROOT\CLSID\{ Your Server’s unique CLSID } = My OPC Server Description

HKEY_CLASSES_ROOT\CLSID\{ Your Server’s unique CLSID }\ProgID = MyVendor.ServerName.1

HKEY_CLASSES_ROOT\CLSID\{ Your Server’s unique CLSID }\LocalServer32 = c:\FULLPATH\OPCserver.exe

HKEY_CLASSES_ROOT\CLSID\{ Your Handler’s unique CLSID }\InprocServer32 = c:\FULLPATH\opchandler.dll

HKEY_CLASSES_ROOT\TypeLib\{ OPC Standard Defined GUID }\1.0\0\win32 = c:\FULLPATH\OPCDisp.tlb

HKEY_CLASSES_ROOT\TypeLib\{ Vendor Defined GUID }\1.0\0\win32 = c:\FULLPATH\MyVendorDisp.tlb

## Registry Entries and DCOM

At this time the prefered (and most flexible) method of using DCOM with an OPC Server is for the client to provide the host name to CoCreateInstanceEx. Note that the CLSID of the target server must also be provided. In general the client will want to obtain this from the PROGID. At this time it is only possible to search the local registry with CLSIDFromPROGID(). For this reason the server vendor will need to provide some way to make the needed entries in the Client machine’s registry. In this case (remote client) the minimum set of entries would be the first 3 or 4 lines from the examples above.

# Description of Data Types, Parameters and Structures

Some structures contain ‘reserved’ words. These are generally inserted to pad structures to be 32 bit aligned.

## Item Definition

The ItemID is the fully qualified definition of a data item in the server, commonly referred to as the WHAT.  No other information is required to identify the data item for the client to be able to read/write values.

The Item definition (ItemID) used in the OPCITEMDEF and elsewhere is a null-terminated string that uniquely identifies an OPC data item.  The syntax of the identifier is server dependent (although it should include only printable UNICODE characters) and it provides a reference or ‘key’ to an ‘item’ in the data source. The item is anything that can be represented by a VARIANT although it is typically a single value such as an analog, digital or string value.

For example, an item such as FIC101 might represent an entire record such as a Fieldbus, Hart Foundation or ProfiBus data structure. Such behavior is specifically allowed but not required by OPC - the return of such structures is considered to be vendor specific behavior.  Alternately FIC101.PV might represent one attribute of a record such as the process value.  This would probably take the form of a double which could be used by any client.

As an extreme example, since the syntax of the item ID is server specific, additional information such as Counts, Engineering Units Scaling and Signal conditioning information could be embedded in the definition string (although this is not recommended).

Examples:

A server which supports access to an existing DCS might support a simple syntax such as

“TIC101.PV”

A server that supports low level access to a PLC might support a syntax such as

“COM1.STATION:42.REG:40001;0,4095,-100.0,+1234.0”

## AccessPath

The AccessPath is intended as a way for the client to provide to the server a suggested data path (e.g. a particular modem or network interface).  It indicates HOW to get the data.

The ITEM ID provides all of the information needed to locate and process a data item. The Access Path is an optional piece of information that can be provided by the client.  Its use is highly server specific but it is intended to allow the client to provide a ‘recommendation’ to the server regarding how to get to the data. As an analogy, if the item id represented a phone number, the access path might represent a request to route the call via satellite (or transatlantic cable or microwave link).  The call will go through regardless of whether you specify an access path and also whether or not the server is able to use that suggested path.

For example, suppose you wanted to access a value in an RTU and had a high speed modem on COM1 and a low speed modem on COM2.  You might specify COM1 as the preferred access path.  Either one will work, but you would prefer to use COM1 if it is available for better performance.

In any case, the use of access path by both the server and the client is optional.  Servers need not provide the function and clients need not use it even if it is provided.

Servers which do not support access paths will completely ignore any passed access path (and will not treat this as an error by the client).  Also, when queried, such servers will always return a null access path for all items.

## Blob

We will discuss why the Blob exists and how it behaves.

The Blob is basically a scratch area for the server to associate with items in order to speed up access to or processing of those items. The exact way in which it is used is server specific.

The idea is that clients refer to items via ASCII strings while internally, to speed up access,  the server will probably need to resolve this string into some internal server specific address; a network address, a pointer into a table, a set of indices or files or register numbers, etc. This address resolution could take considerable time and the resulting internal address could take an arbitrary amount of space. This Blob allows the server to return this internal address and allows the client to save it and to provide the Blob back to the server for future references to this item. The server could use the ‘Blob’ as a ‘hint’ to help find the item more quickly the next time; “The Blob says that last time I looked for this tag I found it ‘here’ - so lets see if its still in that location”. However, in all cases, the ITEM ID is still the ‘key’ to the data. Regardless of the contents of the Blob, the server needs to insure that it is in fact referencing the item referred to by the ITEM ID.

The behavior of the Blob is as follows.

Its use by both client and server is optional. Servers which can perform ‘AddItems’ quickly based just on the item definition should generally not return a Blob.  In cases where servers do return a Blob, clients are free to ignore these Blobs (although this will probably affect the performance of that server).

The Blob is passed to AddItems and ValidateItems and is also returned by the server any time an AddItems or ValidateItems or EnumItemAttributes is done.  The returned Blob may differ in size and content from the one passed.

Note that the server can update the Blob for an item at any time entirely at the server’s discretion (including, for example, whenever the client changes an attribute of an Item).

Proper behavior of a client that wishes to support the Blob is to Enumerate the item attributes to get a fresh copy of the Blobs for each item prior to deleting an item or group and to save that updated copy along with the other application data related to the items.

Comment:

The difference between the server handle and the Blob is that the server handle is fixed in size (DWORD), should not be stored between sessions by the client and that it’s implementation is required since it is the only way to identify items after they have been added.  The Blob is variable in length, is optional and may be stored by the client between sessions.

## Time Stamps

Time stamps are in the form of a FILETIME as this is more compact than other available standard time structures. There are numerous WIN32 functions for converting between various time formats and time zones. Time stamps are always in UTC, this form is beneficial because  it is always increasing and is unambiguous. Time stamps should reflect the best estimate of the time that the data was acquired. If this is not provided by the device itself then it should be provided by the server.

## Variant Data Types for OPC Data Items

Under NT 4.0 and Windows 95 with DCOM support, all VARIANT data types can be marshaled through standard marshalling. Under Automation, types will be coerced to known Automation data types.

NOTE

Real values in the variant (VT_R4, VT_R8) will contain IEEE floating point numbers. Note that the IEEE standard allows certain non numeric values (called NANs) to be stored in this format. While use of such values is rare, they are specifically allowed. If such a value is returned (in the OPCITEMSTATE or in the DATA STREAM to the IAdviseSink) it is required that the QUALITY flag be set to OPC_QUALITY_BAD.

## Constants

### OPCHANDLE

OPCHANDLEs are used in conjunction with both groups and items within groups.  The purpose of handles in OPC is to allow faster access to various objects by both the client and the server.

The exact internal implementation of the server handles is entirely vendor specific. The client should never make any assumptions about the server handles and the server should never make any assumptions about the client handles.

#### Group Handles

OPC groups have both a client and a server handle associated with them.

The server group handle is unique across the server and must be returned when the group is created. The handle is then passed by the client to various methods. The server group handle can be assumed to remain valid until the client Removes the group and free’s all of the interfaces.

It should not be persistently stored by the client as it may be different the next time the OPC group is created.

The client group handle is provided by the client to the server. It can be any value and does not need to be unique. It is included in the data stream sent to IAdviseSink in order to help the client identify the source of the data.

In practice it is expected that a client will assign a unique value to it’s  handle if it intends to use any of the asynchronous functions of the OPC interfaces( including IOPCAsyncIO and IDataObject/IAdviseSink interfaces), since this is the only key to the information that the server gives back to the client via the IAdviseSink interface.

#### Item Handles

OPC items have both a client and a server handle associated with them.

The server item handle is unique within the group and will be returned when the item is created. It is then passed by the client to various methods. The server item handle can be assumed to remain valid until the client Removes the items or Removes the Group containing the items.

It should not be persistently stored by the client as it may be different the next time the OPC Item is created.

The client item handle is provided by the client to the server. It can be any value and does not need to be unique. It is included in the data stream sent to IAdviseSink in order to help the client quickly identify which object in the client application is affected by the changed data.

In practice however it is expected that a client will assign unique values it’s handles if it intends to use any of the asynchronous functions of the OPC interfaces (including IOPCAsyncIO and IDataObject/IAdviseSink interfaces), since this is the only key to the information that the server gives back to the client via the IAdviseSink interface.

## Structures and Masks

### OPCITEMSTATE

This structure is used by IOPCSyncIO::Read

typedef struct {

OPCHANDLE	hClient;

FILETIME	ftTimeStamp;

WORD		wQuality;

WORD		wReserved;

VARIANT	vDataValue;

} OPCITEMSTATE;

| Member | Description |
| --- | --- |
| hClient | the client provided handle for this item |
| ftTimeStamp | UTC TimeStamp for this item's value. If the device cannot provide a timestamp then the server should provide one. |
| wQuality | The quality of this item. |
| vDataValue | The value itself as a variant. |

Comments

The Client should call VariantClear() to free any memory associated with the Variant.

Real values in the variant (VT_R4, VT_R8) will contain IEEE floating point numbers. Note that the IEEE standard allows certain non numeric values (called NANs) to be stored in this format. While use of such values is rare, they are specifically allowed. If such a value is returned it is required that the QUALITY flag be set to OPC_QUALITY_BAD.

### OPCITEMDEF

typedef struct {

[string]	LPWSTR	szAccessPath;

[string]	LPWSTR	szItemID;

BOOL			bActive ;

OPCHANDLE		hClient;

DWORD		dwBlobSize;

[size_is(dwBlobSize)] BYTE * pBlob;

VARTYPE		vtRequestedDataType;

WORD			wReserved;

} OPCITEMDEF;

This structure is used by IOPCItemMgt::AddItems and ValidateItems. The ‘used by’ column below indicates which of these two functions use each member.

| Member | Used by | Description |
| --- | --- | --- |
| szAccessPath | both | The access path the server should associate with this item. By convention a value of NULL specifies that the server should select the access path. Support for this is optional |
| szItemID | both | A null-terminated string that uniquely identifies the OPC data item. See the Item ID discussion and the AddItems function for specific information about the contents of this field. |
| bActive | add | This Boolean value affects the behavior various methods as described elsewhere in this specification. |
| hClient | add | The handle the client wishes to associate with the item. See the OPCHANDLE for more specific information about the contents of this field. |
| dwBlobSize | both | The size of the pBlob for this item. |
| pBlob | both | pBlob is a pointer to the Blob. |
| vtRequestedDataType | both | The data type requested by the client. An error is returned (See Additems or ValidateItems) if the server cannot provide the item in this format. Passing VT_EMPTY means the client will accept the servers canonical datatype. |

Comments

Regarding the datatype; often the same value can be returned in more than one format. For example, a numeric value might be returned as text (VT_BSTR) or real (VT_R8). Such conversions are typically handled in the server by VariantChangeType(). Similarly a status (SCAN status, AUTO/MAN, Alarm, etc.) might be returned as an integer (VT_I4) to be used in animation or color selection or as a string ( VT_BSTR) to be shown directly to the user. This second case is also known as an enumeration and would be vendor specific. Client vendors should note that this specification does not specify what enumeration’s exist or how a server maps the values into strings. Server vendors are strongly encouraged to follow a standard such as FIELDBUS in this area.  See IEnumOPCItemAttributes for more information on this topic.

### OPCITEMRESULT

typedef struct {

OPCHANDLE 		hServer;

VARTYPE		vtCanonicalDataType;

WORD			wReserved;

DWORD		dwAccessRights;

DWORD		dwBlobSize;

[size_is(dwBlobSize)] BYTE * pBlob;

} OPCITEMRESULT;

This structure is used by  IOPCItemMgt::AddItems() and ValidateItems().

| Member | Used by | Description |
| --- | --- | --- |
| hServer | add | The server handle used to refer to this item. |
| vtCanonicalDataType | both | The native data type. The type of data maintained within the server for this item. |
| dwAccessRights | both | Indicates if this item is read only, write only or read/write. This is NOT related to security but rather to the nature of the underlying hardware. See the Access Rights section below. |
| dwBlobSize | both | The size of the Blob for this item. Note that this size may be 0 for servers that do not support or require this feature. |
| pBlob | both | Pointer to the Blob. |

Comments

For AddItems pBlob will always be returned by servers which support this feature.  For ValidateItems it will only be returned if the dwBlobUpdate parameter to ValidateItems is TRUE.

The client software must free the memory for the Blob before freeing the OPCITEMRESULT structure.

### OPCITEMATTRIBUTES

typedef struct {

[string]	LPWSTR	szAccessPath;

[string]	LPWSTR 	szItemID;

BOOL			bActive;

OPCHANDLE 		hClient;

OPCHANDLE 		hServer;

DWORD		dwAccessRights;

DWORD		dwBlobSize;

[size_is(dwBlobSize)] BYTE * pBlob;

VARTYPE		vtRequestedDataType;

VARTYPE		vtCanonicalDataType;

OPCEUTYPE		dwEUType;

VARIANT		vEUInfo;

} OPCITEMATTRIBUTES;

| Member | Description |
| --- | --- |
| szAccessPath | The access path specified by the client. NULL if the server does not support access paths. |
| szItemID | The unique identifier for this item. |
| bActive | FALSE if the item is not currently active, TRUE if the item is currently active |
| hClient | The handle the client has associated with this item. |
| hServer | The handle the server uses to reference this item. |
| dwAccessRights | Indicates if this item is read only, write only or read/write. This is NOT related to security but rather to the nature of the underlying hardware. See the Access Rights section below. |
| dwBlobSize | The size of the pBlob for this item. Note that this size may be 0 for servers that do not support or require this feature. |
| pBlob | Pointer to the Blob. |
| vtRequestedDataType | The data type in which the item's value will be returned. Note that if the requested data type was rejected then this field will return the canonical data type. |
| vtCanonicalDataType | The data type in which the item's value is maintained within the server. |
| dwEUType | Indicate the type of Engineering Units (EU) information (if any) contained in vEUInfo. 0 - No EU information available (vEUInfo will be VT_EMPTY) 1 - Analog - vEUInfo will contain a SAFEARRAY of exactly two doubles (VT_ARRAY ¦ VT_R8) corresponding to the LOW and HI EU range. 2 - Enumerated - vEUInfo will contain a SAFEARRAY of strings (VT_ARRAY ¦ VT_BSTR) which contains a list of strings (Example: “OPEN”, “CLOSE”, “IN TRANSIT”, etc.) corresponding to sequential numeric values (0, 1, 2, etc.) |
| vEUInfo | The VARIANT containing the EU information. See Comments below. |

Comment:

The EU support is optional.  Servers which do not support this will always return EUType as 0 and EUInfo as VT_EMPTY.  EU information (analog or enumerated) can be returned for any value where the canonical type is any of: VT_I2, I4, R4, R8, BOOL, UI1 although in practice some combinations are clearly more likely than others.  Where the item contains an array of values (VT_ARRAY) the EU information will apply to all items in the array (just as the Requested and Canonical Data types apply to all items in the array).

EU information is provided by the server to the client and is essentially Read Only.  OPC Does not provide the client with any control over the EU settings.

For analog EU the information returned represents the ‘usual’ range of the item value.  Sensor or instrument failure or deactivation can result in a returned item value which is actually outside this range.  Client software must be prepared to deal with this.  Similarly a client may attempt to write a value which is outside this range back to the server.  The exact behavior (accept, reject, clamp, etc.) in this case is server dependent however in general servers must be prepared to handle this.

For enumerated EU the information returned represents ‘string lookup table’ corresponding to sequential integer values starting with 0.  The number of values represented is determined by the size of the SAFEARRAY.  Again, robust clients should be prepared to handle item values outside the range of the list and robust servers should be prepared to handle writes of illegal values.

Servers may optionally support Localization of the enumeration.  In this case the server should use the current locale ID of the group.  See IOPCServer::AddGroup and IOPCGroupStateMgt::GetState and SetState.

The client is responsible for freeing the VARIANTs in the OPCITEMATTRIBUTES structure including all elements of any SAFEARRAYs.

Client writers may wish to create and use a common function such as FreeOPCITEMATTRIBUTES(ptr) in order to minimize the chance of memory leaks.

### OPCSERVERSTATUS

typedef struct {

FILETIME 		ftStartTime;

FILETIME 		ftCurrentTime;

FILETIME 		ftLastUpdateTime;

OPCSERVERSTATE	dwServerState;

DWORD		dwGroupCount;

DWORD		dwBandWidth;

WORD			wMajorVersion;

WORD			wMinorVersion;

WORD			wBuildNumber;

WORD			wReserved;

[string]	LPWSTR	szVendorInfo;

} OPCSERVERSTATUS;

This structure used to communicate the status of the server to the client.  This information is provided by the server in the IOPCServer::GetStatus() call.

| Member | Description |
| --- | --- |
| ftStartTime | Time (UTC) the server was started. This is constant for the server instance and is not reset when the server changes states. Each instance of a server should keep the time when the process started. |
| ftCurrentTime | The current time (UTC) as known by the server. |
| ftLastUpdateTime | The time (UTC) the server sent the last data value update to this client. This value is maintained on an instance basis. |
| dwServerState | The current status of the server. Refer to OPC Server State values below. |
| dwGroupCount | The total number of groups (all public and private) being managed by the server. This is mainly for diagnostic purposes. |
| dwBandWidth | The behavior of this field is server specific. A suggested use is that it return the approximate Percent of Bandwidth currently in use by server. If multiple links are in use it could return the ‘worst case’ link. Note that any value over 100% indicates that the aggregate combination of items and UpdateRate is too high. The server may also return 0xFFFFFFFF if this value is unknown. |
| wMajorVersion | The major version of the server software |
| wMinorVersion | The minor version of the server software |
| wBuildNumber | The ‘build number’ of the server software |
| szVendorInfo | Vendor specific string providing additional information about the server. It is recommended that this mention the name of the company and the type of device(s) supported. |

| OPCSERVERSTATE Values | Description |
| --- | --- |
| OPC_STATUS_RUNNING | The server is running normally. This is the usual state for a server |
| OPC_STATUS_FAILED | A vendor specific fatal error has occurred within the server. The server is no longer functioning. The recovery procedure from this situation is vendor specific. An error code of E_FAIL should generally be returned from any other server method. |
| OPC_STATUS_NOCONFIG | The server is running but has no configuration information loaded and thus cannot function normally. Note this state implies that the server needs configuration information in order to function. Servers which do not require configuration information should not return this state. |
| OPC_STATUS_SUSPENDED | The server has been temporarily suspended via some vendor specific method and is not getting or sending data. Note that Quality will be returned as OPC_QUALITY_OUT_OF_SERVICE. |
| OPC_STATUS_TEST | The server is in Test Mode. The outputs are disconnected from the real hardware but the server will otherwise behave normally. Inputs may be real or may be simulated depending on the vendor implementation. Quality will generally be returned normally. |

### Access Rights

This represents the server's ability to access a single OPC data item. Note the low 16 bits of the DWORD are reserved for OPC use and currently include the OPC Access Rights defined in the IDL and described below. The high 16 bits of the DWORD are available for vendor specific use.

| AccessRights Values | Description |
| --- | --- |
| OPC_READABLE | The client can read the data item's value. |
| OPC_WRITEABLE | The client can change the data item's value. |

## OPC Quality flags

These flags represent the quality state for a item's data value. This is intended to be similar to but slightly simpler than the Fieldbus Data Quality Specification (section 4.4.1 in the H1 Final Specifications). This design makes it fairly easy for both servers and client applications to determine how much functionality they want to implement.

The low 8 bits of the Quality flags are currently defined in the form of three bit fields; Quality, Substatus and Limit status.  The 8 Quality bits are arranged as follows:

QQSSSSLL

The high 8 bits of the Quality Word are available for vendor specific use. If these bits are used, the standard OPC Quality bits must still be set as accurately as possible to indicate what assumptions the client can make about the returned data. In addition it is the responsibility of any client interpreting vendor specific quality information to insure that the server providing it uses the same ‘rules’ as the client. The details of such a negotiation are not specified in this standard although a QueryInterface call to the server for a vendor specific interface such as IMyQualityDefinitions is a possible approach.

Details of the OPC standard quality bits follow:

The Quality BitField

| QQ | BIT VALUE | DEFINE | DESCRIPTION |
| --- | --- | --- | --- |
| 0 | 00SSSSLL | Bad | Value is not useful for reasons indicated by the Substatus. |
| 1 | 01SSSSLL | Uncertain | The quality of the value is uncertain for reasons indicated by the Substatus. |
| 2 | 10SSSSLL | N/A | Not used by OPC |
| 3 | 11SSSSLL | Good | The Quality of the value is Good. |

Comment:

A server which supports no quality information must return 3 (Good). It is also acceptable for a server to simply return Bad or Good (0x00 or 0xC0) and to always return 0 for Substatus and limit.

It is recommended that clients minimally check the Quality Bit field of all results (even if they do not check the substatus or limit fields).

Even when a ‘BAD’ value is indicated, the contents of the value field must still be a well defined VARIANT even though it does not contain an accurate value. This is to simplify error handling in client applications. For example, clients are always expected to call VariantClear() on the results of a Sychronous Read. Similarly the IAdviseSink needs to be able to interpret and ‘unpack’ the Value and Data included in the Stream even if that data is BAD.

If the server has no known value to return then some reasonable default should be  returned such as a NULL string or a 0 numeric value.

The Substatus BitField

The layout of this field depends on the value of the Quality Field.

Substatus for BAD Quality:

| SSSS | BIT VALUE | DEFINE | DESCRIPTION |
| --- | --- | --- | --- |
| 0 | 000000LL | Non-specific | The value is bad but no specific reason is known |
| 1 | 000001LL | Configuration Error | There is some server specific problem with the configuration. For example the item is question has been deleted from the configuration. |
| 2 | 000010LL | Not Connected | The input is required to be logically connected to something but is not. This quality may reflect that no value is available at this time, for reasons like the value may have not been provided by the data source. |
| 3 | 000011LL | Device Failure | A device failure has been detected |
| 4 | 000100LL | Sensor Failure | A sensor failure had been detected (the ’Limits’ field can provide additional diagnostic information in some situations.) |
| 5 | 000101LL | Last Known Value | Communications have failed. However, the last known value is available. Note that the ‘age’ of the value may be determined from the TIMESTAMP in the OPCITEMSTATE. |
| 6 | 000110LL | Comm Failure | Communications have failed. There is no last known value is available. |
| 7 | 000111LL | Out of Service | The block is off scan or otherwise locked This quality is also used when the active state of the item or the group containing the item is InActive. |
| 8-15 |  | N/A | Not used by OPC |

Comment

Servers which do not support Substatus should return 0. Note that an ‘old’ value may be  returned with the Quality set to BAD (0) and the Substatus set to 5. This is for consistency with the Fieldbus Specification.  This is the only case in which a client may assume that a ‘BAD’ value is still usable by the application.

Substatus for UNCERTAIN Quality:

| SSSS | BIT VALUE | DEFINE | DESCRIPTION |
| --- | --- | --- | --- |
| 0 | 010000LL | Non-specific | There is no specific reason why the value is uncertain. |
| 1 | 010001LL | Last Usable Value | Whatever was writing this value has stopped doing so. The returned value should be regarded as ‘stale’. Note that this differs from a BAD value with Substatus 5 (Last Known Value). That status is associated specifically with a detectable communications error on a ‘fetched’ value. This error is associated with the failure of some external source to ‘put’ something into the value within an acceptable period of time. Note that the ‘age’ of the value can be determined from the TIMESTAMP in OPCITEMSTATE. |
| 2-3 |  | N/A | Not used by OPC |
| 4 | 010100LL | Sensor Not Accurate | Either the value has ‘pegged’ at one of the sensor limits (in which case the limit field should be set to 1 or 2) or the sensor is otherwise known to be out of calibration via some form of internal diagnostics (in which case the limit field should be 0). |
| 5 | 010101LL | Engineering Units Exceeded | The returned value is outside the limits defined for this parameter. Note that in this case (per the Fieldbus Specification) the ‘Limits’ field indicates which limit has been exceeded but does NOT necessarily imply that the value cannot move farther out of range. |
| 6 | 010110LL | Sub-Normal | The value is derived from multiple sources and has less than the required number of Good sources. |
| 7-15 |  | N/A | Not used by OPC |

Comment

Servers which do not support Substatus should return 0.

Substatus for GOOD Quality:

| SSSS | BIT VALUE | DEFINE | DESCRIPTION |
| --- | --- | --- | --- |
| 0 | 110000LL | Non-specific | The value is good. There are no special conditions |
| 1-5 |  | N/A | Not used by OPC |
| 6 | 110110LL | Local Override | The value has been Overridden. Typically this is means the input has been disconnected and a manually entered value has been ‘forced’. |
| 7-15 |  | N/A | Not used by OPC |

Comment

Servers which do not support Substatus should return 0.

The Limit BitField

The Limit Field is valid regardless of the Quality and Substatus. In some cases such as Sensor Failure it can provide useful diagnostic  information.

| LL | BIT VALUE | DEFINE | DESCRIPTION |
| --- | --- | --- | --- |
| 0 | QQSSSS00 | Not Limited | The value is free to move up or down |
| 1 | QQSSSS01 | Low Limited | The value has ‘pegged’ at some lower limit |
| 2 | QQSSSS10 | High Limited | The value has ‘pegged’ at some high limit. |
| 3 | QQSSSS11 | Constant | The value is a constant and cannot move. |

Comment

Servers which do not support Limit should return 0.

Symbolic Equates are defined for values and masks for these BitFields in the “QUALITY” section of the OPC header files.

## Data Stream Formats

This section describes the data structures associated with the three stream formats used in the IDataObject / IAdviseSink connection.  It also discusses the critical issue of the Packing of these streams and structures.  These formats are also discussed in the Client Side Custom Interface section.

The following table shows the clipboard format names.

| “OPCSTMFORMATDATA” | Used for On Data Change, Refresh and Async Read |
| --- | --- |
| “OPCSTMFORMATDATATIME” | Used for On Data Change, Refresh and Async Read |
| “OPCSTMFORMATWRITECOMPLETE” | Used for Async Write |

Clients and servers must ‘Register’ these stream formats by calling the windows function RegisterClipboardFormat();

### OPCGROUPHEADER

typedef struct {

DWORD	dwSize;

DWORD	dwItemCount;

OPCHANDLE	hClientGroup;

DWORD	dwTransactionID;

HRESULT	hrStatus;

} OPCGROUPHEADER;

This structure can appear at the head of the OPCSTMFORMATDATA or OPCSTMFORMATDATATIME data stream. It is followed by an array of OPCITEMHEADER1s or OPCITEMHEADER2s.

| Member | Description |
| --- | --- |
| dwSize | The Total size of the data stream (the header, all item headers and all data) |
| dwItemCount | The number of Itemheaders which follow. This will vary depending on the number of values being reported. |
| hClientGroup | The client provided handle for the group for which data is being reported. This allows a single OnDataChange handler to identify which of many possible groups are reporting data. |
| dwTransactionID | For normal subscriptions this is 0 For Async operations Refresh or Read this is the transaction ID returned by the method. |
| hrStatus | The status of the asynchronous request (including OnDataChange). This enables error codes (e.g. E_OUTOFMEMORY) to be returned in the case of an asynchronous request failing in the server. A status of S_FALSE should be returned when the read operation was successful, but one or more items has a quality status of BAD or UNCERTAIN. |

Comment

If the hrStatus is any FAILED code then the server must return dwItemCount as 0.

There are no ITEM level HRESULT error codes returned at this time. The only item level status information available to the callback function is the Quality Field.

### OPCITEMHEADER1

typedef struct {

OPCHANDLE	hClient;

DWORD	dwValueOffset;

WORD		wQuality;

WORD		wReserved;

FILETIME	ftTimeStampItem;

} OPCITEMHEADER1;

An array of these structures appears in the stream following the GROUPHEADER for OPCSTMFORMATDATATIME.  The serialized data (in the form of Variants) appears after this array.

| Member | Description |
| --- | --- |
| hClient | The client provided handle associated with this item |
| dwValueOffset | The offset in the data stream (the global memory section) of the serialized variant which contains the data. |
| wQuality | The Quality bits for the data. |
| ftTimeStampItem | The TimeStamp for the data. |

### OPCITEMHEADER2

typedef struct {

OPCHANDLE	hClient;

DWORD	dwValueOffset;

WORD		wQuality;

WORD		wReserved;

} OPCITEMHEADER2;

An array of these structures appears in the stream following the GROUPHEADER for OPCSTMFORMATDATA.  The serialized data (in the form of Variants) appears after this array.

| Member | Description |
| --- | --- |
| hClient | The client provided handle associated with this item |
| dwValueOffset | The offset in the data stream (the global memory section) of the serialized variant which contains the data. |
| wQuality | The Quality bits for the data. |

### OPCGROUPHEADERWRITE

typedef struct {

DWORD	dwItemCount;

OPCHANDLE	hClientGroup;

DWORD	dwTransactionID;

HRESULT	hrStatus;

} OPCGROUPHEADERWRITE;

This structure can appear at the head of the data stream. It is followed by an array of OPCITEMHEADERWRITEs.

| Member | Description |
| --- | --- |
| dwItemCount | The number of Itemheaders which follow. This will vary depending on the number of values being reported. |
| hClientGroup | The client provided handle for the group for which data is being reported. This allows a single OnDataChange handler to identify which of many possible groups are reporting data. |
| dwTransactionID | This is the transaction ID returned by the IOPCAsyncIO::Write method. |
| hrStatus | The status of the asynchronous write request. This enables error codes (e.g. E_OUTOFMEMORY) to be returned in the case of an asynchronous request failing in the server. |

Comment

If the hrStatus is any FAILED code then the server must return dwItemCount as 0.

### OPCITEMHEADERWRITE

typedef struct {

OPCHANDLE	hClient;

HRESULT	dwError;

} OPCITEMHEADERWRITE;

An array of these structures appears in the stream following the GROUPHEADERWRITE.

| Member | Description |
| --- | --- |
| hClient | The client provided handle associated with this item |
| dwError | The HRESULTs for each of the items that was written. |

Comment

The item level HRESULTs for Write are the same as those returned for Sync Write.

### Marshaling the Data (Variants) into the Stream

It is important that all servers marshal the item data into the stream in exactly the same way since the stream itself is exposed to the client.  As mentioned above, the various GROUPHEADERs are written first without padding into the stream followed by as many ITEMHEADERs as needed.  The ITEMHEADERs must be followed by the data itself.  Again the data must be written in exactly the same way without padding by all servers.  This data is always in the form of one of the VARIANT types listed earlier.  For variant types contained within the variant union itself these are written via:

memcpy(dest, source, sizeof(tagVARIANT));

For a BSTR the union is followed without padding by an image of the BSTR. The BSTR image will include the terminating NUL (WIDE char). Note that BSTRs contain WIDE chars which are 2 bytes each. The BSTR starts with a DWORD byte count followed by 'count' bytes of data followed by 2 bytes of 0. Thus the total space required for the BSTR is the number of bytes specified in count + 6 (4 for the DWORD count and 2 for the trailing NUL).

For VT_ARRAY the data is the VARIANT union followed by the SAFEARRAY structure (with one SAFEARRAYBOUND, pvData = NULL) followed by the data items themselves (the contents of the SAFEARRAY’s HGLOBAL). Again, everything including the data items is completely unpadded.

Currently OPC supports only a one dimensional SAFEARRAY.

Clearly any pointers in the SAFEARRAY and VARIANT unions need to be recreated by the receiver when the data is unmarshalled and stored locally.

# Summary of OPC Error Codes

We have attempted to minimize the number of unique errors by identifying common generic problems and defining error codes that can be reused in many contexts. An OPC server should only return those OPC errors that are listed for the various methods in this specification or are standard Microsoft errors. Note that OLE itself will frequently return errors (such as RPC errors) in addition to those listed in this specification.

The most important thing for a client is to check FAILED for any error return. Other than that, (the statements above not withstanding)  a robust, user friendly client should assume that the server may return any error code and should call the GetErrorString function to provide user readable information about those errors.

| Standard COM errors that are commonly used by OPC Servers | Description |
| --- | --- |
| E_FAIL | Unspecified error |
| E_INVALIDARG | The value of one or more parameters was not valid. This is generally used in place of a more specific error where it is expected that problems are unlikely or will be easy to identify (for example when there is only one parameter). |
| E_NOINTERFACE | No such interface supported |
| E_NOTIMPL | Not implemented |
| E_OUTOFMEMORY | Not enough memory to complete the requested operation. This can happen any time the server needs to allocate memory to complete the requested operation. |
| CONNECT_E_ADVISELIMIT | Advise limit exceeded for this object |
| OLE_E_NOCONNECTION | Cannot Unadvise - there is no existing connection |
| DV_E_FORMATETC | Invalid or unregistered Format specified in FORMATETC |

| OPC Specific Errors | Description |
| --- | --- |
| OPC_E_BADRIGHTS | The Items AccessRights do not allow the operation. |
| OPC_E_BADTYPE | The server cannot convert the data between the specified format/ requested data type and the canonical data type. |
| OPC_E_DUPLICATENAME | Duplicate name not allowed. |
| OPC_E_INVALIDCONFIGFILE | The server's configuration file is an invalid format. |
| OPC_E_INVALIDFILTER | The filter string was not valid |
| OPC_E_INVALIDHANDLE | The value of the handle is invalid. Note: a client should never pass an invalid handle to a server. If this error occurs, it is due to a programming error in the client or possibly in the server. |
| OPC_E_INVALIDITEMID | The item ID doesn't conform to the server's syntax. |
| OPC_E_NOTFOUND | Requested Object (e.g. a public group) was not found. |
| OPC_E_PUBLIC | The requested operation cannot be done on a public group. |
| OPC_E_RANGE | The value was out of range. |
| OPC_E_UNKNOWNITEMID | The item ID is not defined in the server address space (on add or validate) or no longer exists in the server address space (for read or write). |
| OPC_E_UNKNOWNPATH | The item's access path is not known to the server. |
| OPC_S_CLAMP | A value passed to WRITE was accepted but the output was clamped. |
| OPC_S_INUSE | The operation cannot be performed because the object is bering referenced. |
| OPC_S_UNSUPPORTEDRATE | The server does not support the requested data rate but will use the closest available rate. |

# OPCError.h

/*++

Module Name:

OpcError.h

Author:

OPC Task Force

Revision History:

Release 1.0A

Removed Unused messages

Added OPC_S_INUSE, OPC_E_INVALIDCONFIGFILE, OPC_E_NOTFOUND

--*/

#ifndef __OPCERROR_H

#define __OPCERROR_H

//

//  Values are 32 bit values laid out as follows:

//

//   3 3 2 2 2 2 2 2 2 2 2 2 1 1 1 1 1 1 1 1 1 1

//   1 0 9 8 7 6 5 4 3 2 1 0 9 8 7 6 5 4 3 2 1 0 9 8 7 6 5 4 3 2 1 0

//  +---+-+-+-----------------------+-------------------------------+

//  |Sev|C|R|     Facility          |               Code            |

//  +---+-+-+-----------------------+-------------------------------+

//

//  where

//

//      Sev - is the severity code

//

//          00 - Success

//          01 - Informational

//          10 - Warning

//          11 - Error

//

//      C - is the Customer code flag

//

//      R - is a reserved bit

//

//      Facility - is the facility code

//

//      Code - is the facility's status code

//

//

//

// MessageId: OPC_E_INVALIDHANDLE

//

// MessageText:

//

//  The value of the handle is invalid.

//

#define OPC_E_INVALIDHANDLE              ((HRESULT)0xC0040001L)

//

// MessageId: OPC_E_BADTYPE

//

// MessageText:

//

//  The server cannot convert the data between the

//  requested data type and the canonical data type.

//

#define OPC_E_BADTYPE                    ((HRESULT)0xC0040004L)

//

// MessageId: OPC_E_PUBLIC

//

// MessageText:

//

//  The requested operation cannot be done on a public group.

//

//

#define OPC_E_PUBLIC                     ((HRESULT)0xC0040005L)

//

// MessageId: OPC_E_BADRIGHTS

//

// MessageText:

//

//  The Items AccessRights do not allow the operation.

//

#define OPC_E_BADRIGHTS                  ((HRESULT)0xC0040006L)

//

// MessageId: OPC_E_UNKNOWNITEMID

//

// MessageText:

//

//  The item is no longer available in the server address space

//

//

#define OPC_E_UNKNOWNITEMID              ((HRESULT)0xC0040007L)

//

// MessageId: OPC_E_INVALIDITEMID

//

// MessageText:

//

//  The item definition doesn't conform to the server's syntax.

//

#define OPC_E_INVALIDITEMID              ((HRESULT)0xC0040008L)

//

// MessageId: OPC_E_INVALIDFILTER

//

// MessageText:

//

//  The filter string was not valid

//

#define OPC_E_INVALIDFILTER              ((HRESULT)0xC0040009L)

//

// MessageId: OPC_E_UNKNOWNPATH

//

// MessageText:

//

//  The item's access path is not known to the server.

//

//

#define OPC_E_UNKNOWNPATH                ((HRESULT)0xC004000AL)

//

// MessageId: OPC_E_RANGE

//

// MessageText:

//

//  The value was out of range.

//

//

#define OPC_E_RANGE                      ((HRESULT)0xC004000BL)

//

// MessageId: OPC_E_DUPLICATENAME

//

// MessageText:

//

//  Duplicate name not allowed.

//

//

#define OPC_E_DUPLICATENAME              ((HRESULT)0xC004000CL)

//

// MessageId: OPC_S_UNSUPPORTEDRATE

//

// MessageText:

//

//  The server does not support the requested data rate

//  but will use the closest available rate.

//

//

#define OPC_S_UNSUPPORTEDRATE            ((HRESULT)0x0004000DL)

//

// MessageId: OPC_S_CLAMP

//

// MessageText:

//

//  A value passed to WRITE was accepted but the output was clamped.

//

#define OPC_S_CLAMP                      ((HRESULT)0x0004000EL)

//

// MessageId: OPC_S_INUSE

//

// MessageText:

//

//  The operation cannot be completed because the

//  object still has references that exist.

//

//

#define OPC_S_INUSE                      ((HRESULT)0x0004000FL)

//

// MessageId: OPC_E_INVALIDCONFIGFILE

//

// MessageText:

//

//  The server's configuration file is an invalid format.

//

#define OPC_E_INVALIDCONFIGFILE          ((HRESULT)0xC0040010L)

//

// MessageId: OPC_E_NOTFOUND

//

// MessageText:

//

//  The server could not locate the requested object.

//

#define OPC_E_NOTFOUND                   ((HRESULT)0xC0040011L)

#endif // OpcError

# Appendix A - IDL Specification

The current files require MIDL compiler 3.00.15 or later and the WIN NT 4.0 release SDK.

Use the command line MIDL /ms_ext /c_ext /app_config opc.idl.

The resulting  OPC.H  file should be included in all clients and servers.

The resulting  OPC_I.C  file defines the interface IDs and should be linked into all clients and servers.

NOTE: This IDL file and the Proxy/Stub generated from it should NEVER be modified in any way. If you add vendor specific interfaces to your server (which is allowed) you must generate a SEPARATE vendor specific IDL file to describe those interfaces and a separate vendor specific ProxyStub DLL to marshall those interfaces.

// OPC.IDL

// REVISION:  5/21/97 08:00 PM (EST)

// VERSIONINFO	1.0.0.0

import "oaidl.idl" ;

typedef enum tagOPCDATASOURCE {

OPC_DS_CACHE = 1,

OPC_DS_DEVICE } OPCDATASOURCE ;

typedef enum tagOPCBROWSETYPE {

OPC_BRANCH = 1,

OPC_LEAF,

OPC_FLAT} OPCBROWSETYPE;

typedef enum tagOPCNAMESPACETYPE {

OPC_NS_HIERARCHIAL = 1,

OPC_NS_FLAT} OPCNAMESPACETYPE;

typedef enum tagOPCBROWSEDIRECTION {

OPC_BROWSE_UP = 1,

OPC_BROWSE_DOWN} OPCBROWSEDIRECTION;

// **NOTE** the 1.0 IDL contained an error for ACCESSRIGHTS.

// They should not have been an ENUM.

// They should have been two mask bits as noted here.

cpp_quote("#define OPC_READABLE    1")

cpp_quote("#define OPC_WRITEABLE   2")

typedef enum tagOPCEUTYPE {

OPC_NOENUM = 0,

OPC_ANALOG,

OPC_ENUMERATED } OPCEUTYPE;

typedef enum tagOPCSERVERSTATE {

OPC_STATUS_RUNNING = 1,

OPC_STATUS_FAILED,

OPC_STATUS_NOCONFIG,

OPC_STATUS_SUSPENDED,

OPC_STATUS_TEST } OPCSERVERSTATE;

typedef enum tagOPCENUMSCOPE { OPC_ENUM_PRIVATE_CONNECTIONS = 1,

OPC_ENUM_PUBLIC_CONNECTIONS,

OPC_ENUM_ALL_CONNECTIONS,

OPC_ENUM_PRIVATE,

OPC_ENUM_PUBLIC,

OPC_ENUM_ALL } OPCENUMSCOPE;

typedef DWORD OPCHANDLE;

typedef struct tagOPCGROUPHEADER {

DWORD       dwSize;

DWORD       dwItemCount;

OPCHANDLE   hClientGroup;

DWORD       dwTransactionID;

HRESULT     hrStatus;

} OPCGROUPHEADER;

typedef struct tagOPCITEMHEADER1 {

OPCHANDLE   hClient;

DWORD       dwValueOffset;

WORD        wQuality;

WORD        wReserved;

FILETIME    ftTimeStampItem;

} OPCITEMHEADER1;

typedef struct tagOPCITEMHEADER2 {

OPCHANDLE   hClient;

DWORD       dwValueOffset;

WORD        wQuality;

WORD        wReserved;

} OPCITEMHEADER2;

typedef struct tagOPCGROUPHEADERWRITE {

DWORD       dwItemCount;

OPCHANDLE   hClientGroup;

DWORD       dwTransactionID;

HRESULT     hrStatus;

} OPCGROUPHEADERWRITE;

typedef struct tagOPCITEMHEADERWRITE {

OPCHANDLE   hClient;

HRESULT     dwError;

} OPCITEMHEADERWRITE;

typedef struct tagOPCITEMSTATE{

OPCHANDLE   hClient;

FILETIME    ftTimeStamp;

WORD        wQuality;

WORD        wReserved;

VARIANT     vDataValue;

} OPCITEMSTATE;

typedef struct tagOPCSERVERSTATUS {

FILETIME       ftStartTime;

FILETIME       ftCurrentTime;

FILETIME       ftLastUpdateTime;

OPCSERVERSTATE dwServerState;

DWORD          dwGroupCount;

DWORD          dwBandWidth;

WORD           wMajorVersion;

WORD           wMinorVersion;

WORD           wBuildNumber;

WORD           wReserved;

[string] LPWSTR         szVendorInfo;

} OPCSERVERSTATUS;

typedef struct tagOPCITEMDEF {

[string]              LPWSTR     szAccessPath;

[string]              LPWSTR     szItemID;

BOOL       bActive ;

OPCHANDLE  hClient;

DWORD      dwBlobSize;

[size_is(dwBlobSize)] BYTE     * pBlob;

VARTYPE    vtRequestedDataType;

WORD       wReserved;

} OPCITEMDEF;

typedef struct tagOPCITEMATTRIBUTES {

[string]              LPWSTR     szAccessPath;

[string]              LPWSTR     szItemID;

BOOL       bActive;

OPCHANDLE  hClient;

OPCHANDLE  hServer;

DWORD      dwAccessRights;

DWORD      dwBlobSize;

[size_is(dwBlobSize)] BYTE     * pBlob;

VARTYPE    vtRequestedDataType;

VARTYPE    vtCanonicalDataType;

OPCEUTYPE  dwEUType;

VARIANT    vEUInfo;

} OPCITEMATTRIBUTES;

typedef struct tagOPCITEMRESULT {

OPCHANDLE  hServer;

VARTYPE    vtCanonicalDataType;

WORD       wReserved;

DWORD      dwAccessRights;

DWORD      dwBlobSize;

[size_is(dwBlobSize)] BYTE     * pBlob;

} OPCITEMRESULT;

//****************************************************

// OPC Quality flags

//

// Masks for extracting quality subfields

// (note ‘status’ mask also includes ‘Quality’ bits)

//

cpp_quote("#define    OPC_QUALITY_MASK            0xC0")

cpp_quote("#define    OPC_STATUS_MASK             0xFC")

cpp_quote("#define    OPC_LIMIT_MASK              0x03")

// Values for QUALITY_MASK bit field

//

cpp_quote("#define    OPC_QUALITY_BAD             0x00")

cpp_quote("#define    OPC_QUALITY_UNCERTAIN       0x40")

cpp_quote("#define    OPC_QUALITY_GOOD            0xC0")

// STATUS_MASK Values for Quality = BAD

//

cpp_quote("#define    OPC_QUALITY_CONFIG_ERROR    0x04")

cpp_quote("#define    OPC_QUALITY_NOT_CONNECTED   0x08")

cpp_quote("#define    OPC_QUALITY_DEVICE_FAILURE  0x0c")

cpp_quote("#define    OPC_QUALITY_SENSOR_FAILURE  0x10")

cpp_quote("#define    OPC_QUALITY_LAST_KNOWN      0x14")

cpp_quote("#define    OPC_QUALITY_COMM_FAILURE    0x18")

cpp_quote("#define    OPC_QUALITY_OUT_OF_SERVICE  0x1C")

// STATUS_MASK Values for Quality = UNCERTAIN

//

cpp_quote("#define    OPC_QUALITY_LAST_USABLE     0x44")

cpp_quote("#define    OPC_QUALITY_SENSOR_CAL      0x50")

cpp_quote("#define    OPC_QUALITY_EGU_EXCEEDED    0x54")

cpp_quote("#define    OPC_QUALITY_SUB_NORMAL      0x58")

// STATUS_MASK Values for Quality = GOOD

//

cpp_quote("#define    OPC_QUALITY_LOCAL_OVERRIDE  0xD8")

// Values for Limit Bitfield

//

cpp_quote("#define    OPC_LIMIT_OK                0x00")

cpp_quote("#define    OPC_LIMIT_LOW               0x01")

cpp_quote("#define    OPC_LIMIT_HIGH              0x02")

cpp_quote("#define    OPC_LIMIT_CONST             0x03")

//****************************************************

//Interface Definitions

//

//****************************************************

[

object,

uuid(39c13a4d-011e-11d0-9675-0020afd8adb3),

pointer_default(unique)

]

interface IOPCServer : IUnknown

{

HRESULT AddGroup(

[in, string]        LPCWSTR     szName,

[in]                BOOL        bActive,

[in]                DWORD       dwRequestedUpdateRate,

[in]                OPCHANDLE   hClientGroup,

[unique, in]        LONG      * pTimeBias,

[unique, in]        FLOAT     * pPercentDeadband,

[in]                DWORD       dwLCID,

[out]               OPCHANDLE * phServerGroup,

[out]               DWORD     * pRevisedUpdateRate,

[in]                REFIID      riid,

[out, iid_is(riid)] LPUNKNOWN * ppUnk

);

HRESULT GetErrorString(

[in]          HRESULT  dwError,

[in]          LCID     dwLocale,

[out, string] LPWSTR * ppString

);

HRESULT GetGroupByName(

[in, string]        LPCWSTR szName,

[in]                REFIID riid,

[out, iid_is(riid)] LPUNKNOWN * ppUnk

);

HRESULT GetStatus(

[out] OPCSERVERSTATUS ** ppServerStatus

);

HRESULT RemoveGroup(

[in] OPCHANDLE hServerGroup,

[in] BOOL      bForce

);

HRESULT CreateGroupEnumerator(

[in] OPCENUMSCOPE dwScope,

[in] REFIID       riid,

[out, iid_is(riid)] LPUNKNOWN* ppUnk

);

}

//****************************************************

[

object,

uuid(39c13a4e-011e-11d0-9675-0020afd8adb3),

pointer_default(unique)

]

interface IOPCServerPublicGroups : IUnknown

{

HRESULT GetPublicGroupByName(

[in, string]        LPCWSTR     szName,

[in]                REFIID      riid,

[out, iid_is(riid)] LPUNKNOWN * ppUnk

);

HRESULT RemovePublicGroup(

[in] OPCHANDLE hServerGroup,

[in] BOOL      bForce

);

}

//****************************************************

[

object,

uuid(39c13a4f-011e-11d0-9675-0020afd8adb3),

pointer_default(unique)

]

interface IOPCBrowseServerAddressSpace: IUnknown

{

HRESULT QueryOrganization(

[out] OPCNAMESPACETYPE  * pNameSpaceType

);

HRESULT ChangeBrowsePosition(

[in]         OPCBROWSEDIRECTION dwBrowseDirection,

[in, string] LPCWSTR            szString

);

HRESULT BrowseOPCItemIDs(

[in]         OPCBROWSETYPE   dwBrowseFilterType,

[in, string] LPCWSTR         szFilterCriteria,

[in]         VARTYPE         vtDataTypeFilter,

[in]         DWORD           dwAccessRightsFilter,

[out]        LPENUMSTRING  * ppIEnumString

);

HRESULT GetItemID(

[in]          LPWSTR   szItemDataID,

[out, string] LPWSTR * szItemID

);

HRESULT BrowseAccessPaths(

[in, string] LPCWSTR        szItemID,

[out]        LPENUMSTRING * ppIEnumString

);

}

//****************************************************

[

object,

uuid(39c13a50-011e-11d0-9675-0020afd8adb3),

pointer_default(unique)

]

interface IOPCGroupStateMgt : IUnknown

{

HRESULT GetState(

[out]         DWORD     * pUpdateRate,

[out]         BOOL      * pActive,

[out, string] LPWSTR    * ppName,

[out]         LONG      * pTimeBias,

[out]         FLOAT     * pPercentDeadband,

[out]         DWORD     * pLCID,

[out]         OPCHANDLE * phClientGroup,

[out]         OPCHANDLE * phServerGroup

);

HRESULT SetState(

[unique, in]  DWORD     * pRequestedUpdateRate,

[out]         DWORD     * pRevisedUpdateRate,

[unique, in]  BOOL      * pActive,

[unique, in]  LONG      * pTimeBias,

[unique, in]  FLOAT     * pPercentDeadband,

[unique, in]  DWORD     * pLCID,

[unique, in]  OPCHANDLE * phClientGroup

);

HRESULT SetName(

[in, string] LPCWSTR szName

);

HRESULT CloneGroup(

[in, string]        LPCWSTR     szName,

[in]                REFIID      riid,

[out, iid_is(riid)] LPUNKNOWN * ppUnk

);

}

//****************************************************

[

object,

uuid(39c13a51-011e-11d0-9675-0020afd8adb3),

pointer_default(unique)

]

interface IOPCPublicGroupStateMgt : IUnknown

{

HRESULT GetState(

[out] BOOL * pPublic

);

HRESULT MoveToPublic(

void

);

}

//****************************************************

[

object,

uuid(39c13a52-011e-11d0-9675-0020afd8adb3),

pointer_default(unique)

]

interface IOPCSyncIO : IUnknown

{

HRESULT Read(

[in]                        OPCDATASOURCE   dwSource,

[in]                        DWORD           dwNumItems,

[in, size_is(dwNumItems)]   OPCHANDLE     * phServer,

[out, size_is(,dwNumItems)] OPCITEMSTATE ** ppItemValues,

[out, size_is(,dwNumItems)] HRESULT      ** ppErrors

);

HRESULT Write(

[in]                        DWORD        dwNumItems,

[in, size_is(dwNumItems)]   OPCHANDLE  * phServer,

[in, size_is(dwNumItems)]   VARIANT    * pItemValues,

[out, size_is(,dwNumItems)] HRESULT   ** ppErrors

);

}

//****************************************************

[

object,

uuid(39c13a53-011e-11d0-9675-0020afd8adb3),

pointer_default(unique)

]

interface IOPCAsyncIO : IUnknown

{

HRESULT Read(

[in]                        DWORD           dwConnection,

[in]                        OPCDATASOURCE   dwSource,

[in]                        DWORD           dwNumItems,

[in, size_is(dwNumItems)]   OPCHANDLE     * phServer,

[out]                       DWORD         * pTransactionID,

[out, size_is(,dwNumItems)] HRESULT      ** ppErrors

);

HRESULT Write(

[in]                        DWORD       dwConnection,

[in]                        DWORD       dwNumItems,

[in, size_is(dwNumItems)]   OPCHANDLE * phServer,

[in, size_is(dwNumItems)]   VARIANT   * pItemValues,

[out]                       DWORD     * pTransactionID,

[out, size_is(,dwNumItems)] HRESULT  ** ppErrors

);

HRESULT Refresh(

[in]  DWORD           dwConnection,

[in]  OPCDATASOURCE   dwSource,

[out] DWORD         * pTransactionID

);

HRESULT Cancel(

[in] DWORD dwTransactionID

);

}

//****************************************************

[

object,

uuid(39c13a54-011e-11d0-9675-0020afd8adb3),

pointer_default(unique)

]

interface IOPCItemMgt: IUnknown

{

HRESULT AddItems(

[in]                        DWORD            dwNumItems,

[in, size_is(dwNumItems)]   OPCITEMDEF     * pItemArray,

[out, size_is(,dwNumItems)] OPCITEMRESULT ** ppAddResults,

[out, size_is(,dwNumItems)] HRESULT       ** ppErrors

);

HRESULT ValidateItems(

[in]                        DWORD             dwNumItems,

[in, size_is(dwNumItems)]   OPCITEMDEF      * pItemArray,

[in]                        BOOL              bBlobUpdate,

[out, size_is(,dwNumItems)]OPCITEMRESULT ** ppValidationResults,

[out, size_is(,dwNumItems)] HRESULT        ** ppErrors

);

HRESULT RemoveItems(

[in]                        DWORD        dwNumItems,

[in, size_is(dwNumItems)]   OPCHANDLE  * phServer,

[out, size_is(,dwNumItems)] HRESULT   ** ppErrors

);

HRESULT SetActiveState(

[in]                        DWORD        dwNumItems,

[in, size_is(dwNumItems)]   OPCHANDLE  * phServer,

[in]                        BOOL         bActive,

[out, size_is(,dwNumItems)] HRESULT   ** ppErrors

);

HRESULT SetClientHandles(

[in]                        DWORD        dwNumItems,

[in, size_is(dwNumItems)]   OPCHANDLE  * phServer,

[in, size_is(dwNumItems)]   OPCHANDLE  * phClient,

[out, size_is(,dwNumItems)] HRESULT   ** ppErrors

);

HRESULT SetDatatypes(

[in]                        DWORD        dwNumItems,

[in, size_is(dwNumItems)]   OPCHANDLE  * phServer,

[in, size_is(dwNumItems)]   VARTYPE    * pRequestedDatatypes,

[out, size_is(,dwNumItems)] HRESULT   ** ppErrors

);

HRESULT CreateEnumerator(

[in]                REFIID      riid,

[out, iid_is(riid)] LPUNKNOWN * ppUnk

);

}

//****************************************************

[

object,

uuid(39c13a55-011e-11d0-9675-0020afd8adb3),

pointer_default(unique)

]

interface IEnumOPCItemAttributes : IUnknown

{

HRESULT Next(

[in]  ULONG celt,

[out, size_is(,*pceltFetched)] OPCITEMATTRIBUTES ** ppItemArray,

[out] ULONG * pceltFetched

);

HRESULT Skip(

[in] ULONG celt

);

HRESULT Reset(

void

);

HRESULT Clone(

[out] IEnumOPCItemAttributes ** ppEnumItemAttributes

);

}

# Appendix B - ODL Specification

//

// OPCDISP.ODL

// Previous Revision: 8/28/96 8:00 PM

// Revision: 6/19/97 8:00 PM - Change boolean to BOOL

//           The use of ‘boolean’ was an error and prevented dual

//           interfaces from functioning properly.

//

//

// This is the ODL file for the OPC IDispatch Automation interfaces.

//

// This file will be processed by the Make Type Library (mktyplib) tool

// or by MIDL 3.00.75 (or newer)

// to produce the type library (OPCDisp.tlb).

#define DISPID_NEWENUM -4

[

uuid(39c13a56-011e-11d0-9675-0020afd8adb3),

version(1.0),

helpstring("OPCDisp")

]

library OPCDisp

{

importlib("stdole32.tlb");

[

uuid(39c13a57-011e-11d0-9675-0020afd8adb3),

dual,

oleautomation

]

interface IOPCServerDisp : IDispatch

{

//

// Properties

//

[ propget ]

HRESULT Count(

[out, retval] long * pCount

);

[ propget,

restricted,

id( DISPID_NEWENUM )

]

HRESULT _NewEnum(

[out, retval] IUnknown ** ppUnk

);

[ propget ]

HRESULT StartTime(

[out, retval] DATE * pStartTime

);

[ propget ]

HRESULT CurrentTime(

[out, retval] DATE * pCurrentTime

);

[ propget ]

HRESULT LastUpdateTime(

[out, retval] DATE * pLastUpdateTime

);

[ propget ]

HRESULT MajorVersion(

[out, retval] short * pMajorVersion

);

[ propget ]

HRESULT MinorVersion(

[out, retval] short * pMinorVersion

);

[ propget ]

HRESULT BuildNumber(

[out, retval] short * pBuildNumber

);

[ propget ]

HRESULT VendorInfo(

[out, retval] BSTR * pVendorInfo

);

//

// Methods

//

HRESULT Item(

[in]          VARIANT      Item,

[out, retval] IDispatch ** ppDisp

);

HRESULT AddGroup(

[in]           BSTR         Name,

[in]           BOOL         Active,

[in]           long         ReqestedUpdateRate,

[in]           long         ClientGroupHandle,

[in]           float       * pPercentDeadband,

[in]           long         LCID,

[out]          long       * pServerGroupHandle,

[out]          long       * pRevisedUpdateRate,

[in, optional] VARIANT    * pTimeBias,

[out, retval]  IDispatch ** ppDisp

);

HRESULT GetErrorString(

[in]          long   Error,

[in]          long   Locale,

[out, retval] BSTR * ErrorString

);

HRESULT GetGroupByName(

[in]          BSTR         Name,

[out, retval] IDispatch ** ppDisp

);

HRESULT RemoveGroup(

[in] long    ServerGroupHandle,

[in] BOOL    Force

);

HRESULT SaveConfig(

[in] BSTR FileName

);

HRESULT LoadConfig(

[in] BSTR FileName

);

HRESULT SetEnumeratorType(

[in] long  Scope,

[in] short Type

);

}

[

uuid(39c13a58-011e-11d0-9675-0020afd8adb3),

dual,

oleautomation

]

interface IOPCServerPublicGroupsDisp : IDispatch

{

//

// Methods

//

HRESULT GetPublicGroupByName(

[in]          BSTR         Name,

[out, retval] IDispatch ** ppDisp

);

HRESULT RemovePublicGroup(

[in] long    ServerGroupHandle,

[in] BOOL    Force

);

}

[

uuid(39c13a59-011e-11d0-9675-0020afd8adb3),

dual,

oleautomation

]

interface IOPCBrowseServerAddressSpaceDisp : IDispatch

{

//

// Properties

//

[ propget,

restricted,

id( DISPID_NEWENUM )

]

HRESULT _NewEnum(

[out, retval] IUnknown ** ppUnk

);

[ propget ]

HRESULT Organization(

[out, retval] long * pNameSpaceType

);

//

// Methods

//

HRESULT ChangeBrowsePosition(

[in] long BrowseDirection,

[in] BSTR Position

);

HRESULT SetItemIDEnumerator(

[in]          long         BrowseFilterType,

[in]          BSTR         FilterCriteria,

[in]          VARIANT      DataTypeFilter,

[in]          long         AccessRightsFilter

);

HRESULT GetItemIDString(

[in]          BSTR   ItemDataID,

[out, retval] BSTR * ItemID

);

HRESULT SetAccessPathEnumerator(

[in]          BSTR         ItemID

);

}

[

uuid(39c13a5a-011e-11d0-9675-0020afd8adb3),

dual,

oleautomation

]

interface IOPCItemMgtDisp : IDispatch

{

//

// Properties

//

[ propget ]

HRESULT Count(

[out, retval] long * pCount

);

[ propget,

restricted,

id( DISPID_NEWENUM )

]

HRESULT _NewEnum(

[out, retval] IUnknown ** ppUnk

);

//

// Methods

//

HRESULT Item(

[in]          VARIANT      ItemSpecifier,

[out, retval] IDispatch ** ppDisp

);

HRESULT AddItems(

[in]                long      NumItems,

[in]                VARIANT   ItemIDs,

[in]                VARIANT   ActiveStates,

[in]                VARIANT   ClientHandles,

[out]               VARIANT * pServerHandles,

[out]               VARIANT * pErrors,

[out]               VARIANT * pItemObjects,

[in, optional]      VARIANT   AccessPaths,

[in, optional]      VARIANT   RequestedDataTypes,

[in, out, optional] VARIANT * pBlobs,

[out, optional]     VARIANT * pCanonicalDataTypes,

[out, optional]     VARIANT * pAccessRights

);

HRESULT ValidateItems(

[in]                long      NumItems,

[in]                VARIANT   ItemIDs,

[out]               VARIANT * pErrors,

[in, optional]      VARIANT   AccessPaths,

[in, optional]      VARIANT   RequestedDataTypes,

[in, optional]      VARIANT BlobUpdate,

[in, out, optional] VARIANT * pBlobs,

[out, optional]     VARIANT * pCanonicalDataTypes,

[out, optional]     VARIANT * pAccessRights

);

HRESULT RemoveItems(

[in]  long      NumItems,

[in]  VARIANT   ServerHandles,

[out] VARIANT * pErrors,

[in]  BOOL      Force

);

HRESULT SetActiveState(

[in]  long      NumItems,

[in]  VARIANT   ServerHandles,

[in]  BOOL      ActiveState,

[out] VARIANT * pErrors

);

HRESULT SetClientHandles(

[in]  long      NumItems,

[in]  VARIANT   ServerHandles,

[in]  VARIANT   ClientHandles,

[out] VARIANT * pErrors

);

HRESULT SetDatatypes(

[in]  long      NumItems,

[in]  VARIANT   ServerHandles,

[in]  VARIANT   RequestedDataTypes,

[out] VARIANT * pErrors

);

}

[

uuid(39c13a5b-011e-11d0-9675-0020afd8adb3),

dual,

oleautomation

]

interface IOPCGroupStateMgtDisp : IDispatch

{

//

// Properties

//

[ propget ]

HRESULT ActiveStatus(

[out, retval] BOOL * pActiveStatus

);

[ propput ]

HRESULT ActiveStatus(

[in] BOOL ActiveStatus

);

[ propget ]

HRESULT ClientGroupHandle(

[out, retval] long * phClientGroupHandle

);

[ propput ]

HRESULT ClientGroupHandle(

[in] long ClientGroupHandle

);

[ propget ]

HRESULT ServerGroupHandle(

[out, retval] long * phServerGroupHandle

);

[ propget ]

HRESULT Name(

[out, retval] BSTR * pName

);

[ propput ]

HRESULT Name(

[in] BSTR Name

);

[ propget ]

HRESULT UpdateRate(

[out, retval] long * pUpdateRate

);

[ propput ]

HRESULT UpdateRate(

[in] long UpdateRate

);

[ propget ]

HRESULT TimeBias(

[out, retval] long * pTimeBias

);

[ propput ]

HRESULT TimeBias(

[in] long TimeBias

);

[ propget ]

HRESULT PercentDeadBand(

[out, retval] float * pPercentDeadBand

);

[ propput ]

HRESULT PercentDeadBand(

[in] float PercentDeadBand

);

[ propget ]

HRESULT LCID(

[out, retval] long * pLCID

);

[ propput ]

HRESULT LCID(

[in] long LCID

);

//

// Methods

//

HRESULT CloneGroup(

[in, optional] VARIANT      Name,

[out, retval]  IDispatch ** ppDisp

);

}

[

uuid(39c13a5c-011e-11d0-9675-0020afd8adb3),

dual,

oleautomation

]

interface IOPCSyncIODisp : IDispatch

{

//

// Properties

//

//

// Methods

//

HRESULT OPCRead(

[in]            short     Source,

[in]            long      NumItems,

[in]            VARIANT   ServerHandles,

[out]           VARIANT * pValues,

[out, optional] VARIANT * pQualities,

[out, optional] VARIANT * pTimeStamps,

[out, optional] VARIANT * pErrors

);

HRESULT OPCWrite(

[in]            long      NumItems,

[in]            VARIANT   ServerHandles,

[in]            VARIANT   Values,

[out, optional] VARIANT * pErrors

);

}

[

uuid(39c13a5d-011e-11d0-9675-0020afd8adb3),

dual,

oleautomation

]

interface IOPCAsyncIODisp : IDispatch

{

//

// Properties

//

//

// Methods

//

HRESULT AddCallbackReference(

[in]          long        Context,

[in]          IDispatch * pCallback,

[out, retval] long      * pConnection

);

HRESULT DropCallbackReference(

[in] long Connection

);

HRESULT OPCRead(

[in]            short     Source,

[in]            long      NumItems,

[in]            VARIANT   ServerHandles,

[out, optional] VARIANT * pErrors,

[out, retval]   long    * pTransactionID

);

HRESULT OPCWrite(

[in]            long      NumItems,

[in]            VARIANT   ServerHandles,

[in]            VARIANT   Values,

[out, optional] VARIANT * pErrors,

[out, retval]   long    * pTransactionID

);

HRESULT Cancel(

[in] long TransactionID

);

HRESULT Refresh(

[in]          short   Source,

[out, retval] long  * pTransactionID

);

}

[

uuid(39c13a5e-011e-11d0-9675-0020afd8adb3),

dual,

oleautomation

]

interface IOPCPublicGroupStateMgtDisp : IDispatch

{

//

// Properties

//

[ propget ]

HRESULT State(

[out, retval] BOOL * pPublic

);

//

// Methods

//

HRESULT MoveToPublic(

void

);

}

[

uuid(39c13a5f-011e-11d0-9675-0020afd8adb3),

dual,

oleautomation

]

interface IOPCItemDisp : IDispatch

{

//

// Properties

//

[ propget ]

HRESULT AccessPath(

[out, retval] BSTR * pAccessPath

);

[ propget ]

HRESULT AccessRights(

[out, retval] long * pAccessRights

);

[ propget ]

HRESULT ActiveStatus(

[out, retval] BOOL * pActiveStatus

);

[ propput ]

HRESULT ActiveStatus(

[in] BOOL ActiveStatus

);

[ propget ]

HRESULT Blob(

[out, retval] VARIANT * pBlob

);

[ propget ]

HRESULT ClientHandle(

[out, retval] long * phClient

);

[ propput ]

HRESULT ClientHandle(

[in] long Client

);

[ propget ]

HRESULT ItemID(

[out, retval] BSTR * pItemID

);

[ propget ]

HRESULT ServerHandle(

[out, retval] long * pServer

);

[ propget ]

HRESULT RequestedDataType(

[out, retval] short * pRequestedDataType

);

[ propput ]

HRESULT RequestedDataType(

[in] short RequestedDataType

);

[ propget ]

HRESULT Value(

[out, retval] VARIANT * pValue

);

[ propput ]

HRESULT Value(

[in] VARIANT NewValue

);

[ propget ]

HRESULT Quality(

[out, retval] short * pQuality

);

[ propget ]

HRESULT Timestamp(

[out, retval] DATE * pTimeStamp

);

[ propget ]

HRESULT ReadError(

[out, retval] long * pError

);

[ propget ]

HRESULT WriteError(

[out, retval] long * pError

);

[ propget ]

HRESULT EUType(

[out, retval] short * pError

);

[ propget ]

HRESULT EUInfo(

[out, retval] VARIANT * pError

);

//

// Methods

//

HRESULT OPCRead(

[in]            short     Source,

[out]           VARIANT * pValue,

[out, optional] VARIANT * pQuality,

[out, optional] VARIANT * pTimestamp

);

HRESULT OPCWrite(

[in] VARIANT NewValue

);

}

[

uuid(39c13a60-011e-11d0-9675-0020afd8adb3),

helpstring("OPC Group Class")

]

coclass Group

{

[default] interface IOPCItemMgtDisp;

interface IOPCGroupStateMgtDisp;

interface IOPCSyncIODisp;

interface IOPCAsyncIODisp;

interface IOPCPublicGroupStateMgtDisp;

}

[

uuid(39c13a61-011e-11d0-9675-0020afd8adb3),

helpstring("OPC Item Class")

]

coclass Item

{

[default] interface IOPCItemDisp;

}

};

SELFREG_E_CLASS and SELFREG_E_TYPELIB are defined in the OLE Control’s header OLECTL.H.